Tags are utilised on the CBESS project to convey information about a particular situation or task as shown below.

All sections of tags shall be completed and signed by the relevant person before deemed valid

| TAG TYPE | TAG USAGE |
| --- | --- |
| BOUNDARY ISOLATION TAG | - Must be placed in conjunction with a boundary isolation lock - Must also be placed on adjacent disconnected equipment, tag details must match on both sides. - Can only be placed or removed by a Personal Isolation Officer - Can only be removed once the equipment isolated is cleared for energisation by an authorised isolation officer - Removing a boundary isolation tag that is not attached to a boundary isolation lock is considered a serious breach of procedure. |
| PERSONAL DANGER TAG | - Used for personal & permit isolations (Unless lock number is registered on permit) - Placed on a personal isolation lock by a lock holder before lock is attached to an isolation point or lockout device - Only the person who placed the lock/tag is authorized to remove it, unless exceptional circumstances apply |
| COMMISSIONING AND TESTING TAG | - Used to identify areas or equipment that are under commissioning control - Must be used in conjunction with a commissioning lock when placing and verifying simple isolations. - Electrical equipment may be identified by a Commissioning in Progress adhesive label, which shall be the same design as the tag. - Equipment must not be operated and / or the tag removed without permission from the commissioning manager or authorised nominee |
| ISOLATION TAG | - Used to identify a particular isolation point - Can only be placed and removed by an Authorised Isolation Officer - Proof that equipment isolation has been carried out - Must not be removed whilst personal danger tags are present |
| OUT OF SERVICE TAG | - Used to identify faulty equipment - Can be placed by any personnel - Can only be removed by an authorised repair agent once repairs are underway or have been completed |
| INFORMATION TAG | - Used to convey general information regarding a particular area or task such as the reason for barricading or an identified hazard - Can be placed and removed by any personnel involved with the task in question - Information shall be updated as required and tag shall be removed when the information displayed is no longer valid |

Once tag is no longer required the tag is to be torn in half and disposed of in a correct manner