## Document Cover Page
Contractor Document Cover Page
Collie Battery Energy Storage System Balance of Plant Controlled Document
Document Information
Synergy Document No:* | [7 empty] | Rev: | 3
Contract No: | [7 empty] | Total no. of pages: (incl Doc Cover Sheet)
Document Title: * |  |  | Collie Battery Energy Storage System BOP-CRAW-Project Risk Register
Tag No:
Vendor Document No: * |  |  | N/A |  |  |  |  | Rev: | N/A
Revision History
Contractor shall ensure that documents have been fully checked and approved prior to submission to Synergy |  |  | Prepared | M Bentley | Checked | D Gray |  | Approved | D Gray
|  |  | Date |  | Date |  |  | Date
Notes: |  |  |  |  | Supplier/Contractors name, Address and Logo:
Company Logo here
REVIEWED BY SYNERGY
1 | Accepted. Work may proceed
2 | Accepted. Work may proceed. Submit Final Deliverable.
3 | Accepted. Work may proceed subject to incorporation of changes indicated.
4 | Not accepted. Revise and Resubmit. Work may not proceed.
5 | Review Not Required. Work may proceed.
1) Deliverables includes document, drawing, sketch and/or any other support for which a Review is needed. 2) Permission to proceed does not constitute approval of design details, calculations, analyses, test methods or material developed or selected by the Contractor. 3) This review: (a) has not included a dimensional check; and (b) does not relieve the Vendor/Contractor from full compliance with Contractual obligations.
[5 empty] | Rev | Date | Description
Date: |  | By: |  |  | Revisions to Synergy Document No.

## Cover Page (hidden)
SHE Risk Register Details
Business |  |  | SCEE Electrical
Project |  |  | Synergy Collie Battery Energy Storage System Balance of Plant
Purpose |  |  | Identify key hazards and controls applicable to full scope of the project
Comments |  |  | This document will evolve as the project progresses.
Risk Owner |  |  | Project Manager - David Gray
Version | Date | Modifications (List changes made to previous version - N/A for original version) |  | Risk Team (List Names and Positions of each person involved in development / review) | Author | Approved by (Risk Owner) | Next Revision Date
1 | 2024-05-24 | Initial document from Construction Risk Assessment Review meeting |  |  | Mike Bentley | Dave Gray | 2024-07-10
2 | 2024-07-10 | Use of Telehandler to move and place culverts added |  |  | Aled Evans | Dave Gray | TBA
3 | 2024-08-20 | Working near water added |  |  | Aled Evans | Dave Gray
4.0 | 2024-08-23 | Entering, working and emergency rescue from RMU units added |  |  | Aled Evans | Dave Gray
5.0 | 2024-09-05 | Use of P2 masks when grinding conduit to culvert joints added |  |  | Aled Evans | Dave Gray
6.0 | 2024-09-10 | Battery transport to site, Crane assembly, Crane operations (Battery landing) added |  |  | Aled Evans | Dave Gray
7.0 | 2024-09-19 | Battery isolation, guarding of open conduit box outs added |  |  | Aled Evans | Dave Gray
8.0 | 2024-11-13 | Steelworks and Tilt up panel construction added |  |  | Aled Evans | Dave Gray
9.0 | 2025-02-20 | Installation of Roof Sheeting |  |  | Arin Abrahams | Dave Gray | TBA

## Look Ups
| 1 | 2 | 3 | 4 | 5
Almost Certain | Medium 6 | Medium 10 | High 16 | Critical 21 | Critical 25
Likely | Low 4 | Medium 9 | High 15 | Critical 20 | Critical 24
Possible | Low 3 | Medium 8 | High 14 | High 18 | Critical 23
Unlikely | Low 2 | Medium 7 | Medium 12 | High 17 | Critical 22
Rare | Low 1 | Low 5 | Medium 11 | Medium 13 | High 19
Minor | 1
Moderate | 2
Major | 3
Severe | 4
Catastrophic | 5
Rare
Unlikely
Possible
Likely
Almost Certain

## Mobilisation & Establishment
Register Type | Project Risk Register
Project(s) | CBESS BOP
Approved by
Task / Activity | Hazard | Risk (un-wanted event) | Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
MOBILISATION
Mobilisation of personnel | Unqualified personnel | Inadequate competency of personnel. Breach of licensing regulations | SCEE-TR-TD-PRO-0001 Training and Competency 201047-TR-MAT-001 Training Needs Analysis | Reference and competency checks Training needs analysis / matrix Training Matrix to includes role specific requirements Project induction Project site orientation for new starters. Supervisors to conduct relevant Safe Work Practice assessments / observations with new starters. First Swing Program for new starters. Family Star Program | Moderate | Unlikely | 2 | M7
Mobilisation of subcontractors | Contractor engagement | Unfamiliarity with SCEE/Site procedures. Conducting work unsafely or in conflict with site or Principal procedures. High risk and/or specialised tasks. Introduced hazards to the workplace. | SCEE-TR-TD-PRO-0001 Training and Competency 201047-TR-MAT-001 Training Needs Analysis | Contractor and Supplier Management Procedure Contractor pre-qualification process in Felix and approved prior to mobilisation. Contractor induction process, including site inductions Project site orientation for new starters. Star Inspections | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Mobilisation of equipment | Poor vehicle hygiene | Spread of weeds, seeds Damage to environment caused by cross contamination | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-FM-0020 Mobilisation-Demobilisation Weed Hygiene Certificate | Plant Pre acceptance Checks prior to mobilisation, including weed and seed inspection Decontamination of vehicles where required | Moderate | Rare | 2 | L5
Establishment / use of project laydown yard & site office | Hostile third party gaining access to yard / site office | Theft / security incident | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan 201074-SE-PLN-004 CBESS Traffic Management Plan 201074-SM-PRO-001 Site Security Procedure | Laydown yard to be fully fenced (and secured after hours) Temporary Fencing will be provided by SCEE other fencing to be undertaken by Principal. Security lighting to be on in hours of darkness Lighting towers for site. Security Company - Including Out of hours security and Mobile Patrols Lone worker communication protocols Lock plant and equipment supervision to secure keys in main office. Fuel farm to be locked after hours | Major | Unlikely | 3 | M12
Traffic Management | Close proximity to CPS and adjacent properties | Disruption to project from traffic external to project. | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan WF SMP 201074-SE-PLN-004 CBESS Traffic Management Plan | Project Induction Access to site to be via security/gate entry Site signage clearly defining project boundary and entry requirements | Minor | Unlikely | 1 | L2 |  | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Public Access | Security | Members of the public inadvertently gaining access to yard / site office | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-004 CBESS Traffic Management Plan 201074-SM-PRO-001 Site Security Procedure | Principal contractor responsible for project security. Site boundaries secured with fencing in place to discourage access. Signage in place at access points with call up/approval process Card access system to be installed with turnstile/boom gate | Major | Unlikely | 3 | M12
Overhead Services on site | Powerlines / Conductors at car park/laydown area and inside of the project boundaries. | Possible MAD breach if using extended crane booms/excavators (note: only until existing line is de-energised & removed) | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-004 CBESS Traffic Management Plan | Divert vehicles and plant clear of overhead services on site where machine envelope will encroach MAD. Identify no lifting / no tipping / No raised excavator boom zones within MADS. Traffic Control Plans - (TCP) Provided in Pre-starts SWMS & JHA HV Access Permit (Western Power) if required Install Signage adjacent to the overhead services. Create conditions of delivery note to be sent to external parties due to access the property Project Induction 330KV conductor height known in car park - 15 metres 330kV conductor height known within site boundary - TBA | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Offices and Amenities | Toilet / hand washing amenities - availability and suitability | Exposure to biological hazard (illness / disease) Environmental damage caused by chemical spills | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan 201074-SE-PLN-003 CBESS Waste Management Plan | Service and maintain ablution facilities regularly Pump out and remove waste via a licensed contractor Install level alarms in black water tanks to prevent overflows Ensure spill kit is kept on site and train personnel in their use Dispose of waste according to local regulations Secure hazardous chemicals in offices and ablution areas with bunds and tightly fitted lids during transport and storage | Moderate | Rare | 2 | L5 |  | Site First Aiders Site Medic Emergency Channel 39
Site Work | Poor Fitness for Work | Injury / illness as a result of impaired fitness for work | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-HR-HR-POL-004 Fitness for Work Policy | Daily BAC Testing. D&A testing program (pre-employment, random, for-cause, blanket) Conditions of employment Employee Assistance Program (EAP) | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Driving / Mobilisation of plant & equipment from site office to work site | Vehicle vs vehicle / vehicle vs pedestrian collision | Psychological and/or physical injuries Property damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-004 CBESS Traffic Management Plan SCEE-HR-HR-POL-0011 Motor Vehicle Policy | Site Induction Traffic Management Plan SWMS JHA Take 5 Drivers must have a current full driver’s license for the appropriate class of vehicle Compliance with road traffic laws Maintenance schedule for fleet vehicles Daily pre-start check. Defects to be reported to workshop to enable repairs Vehicle registration and insurance Fleet cars fitted with First Aid kit Segregated pedestrian walkways Site Speed Limit Limited parking of light vehicles on site | Major | Unlikely | 3 | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Loading / Unloading | Unrestrained / Incorrectly restrained Loads | Load shifting during transport causing damage to equipment, other vehicles, surrounding property, persons | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SM-GUI-0001 SCEE Loading and Unloading Guidance Note SCEE-BS-HS-SWM-0022 Loading and Unloading of Material Plant and Equipment on Site | Operators / Drivers to check Trucks, trailers must not be loaded such that rated mass limits and manufacturer’s individual component ratings (i.e. front axles, springs etc) are exceeded. Prevent overhanging loads, the load must not project more than 1.0m in front of or behind the truck or trailer or more than 150mm from the sides. Load restraint systems used on vehicles or trailers should be capable of preventing the load from shifting during acceleration, cornering, and braking. Delivery drivers are to be kept clear of unloading / loading and remain in safe place or in the vehicle cab. They may untie and secure loads. Barricade unloading zones or have a spotter in place. Prevent anyone from falling off trucks by fitted with gates where possible to provide fall protection when the load is being slung prior to lifting by crane. Where trailers are not fitted with gates, webbing barriers must be installed where possible along the length of the trailer to provide a fall prevention barrier. SWMS JHA & Take 5 Only competent persons to load/unload plant & equipment All loads to be checked prior to mobilisation of vehicle Regular checks to be done on all tie down straps and chains by accredited person | Major | Rare | 3 | M11 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
SITE SET-UP & ACCESS
Cultural Heritage | Disturbing cultural heritage items or areas | Unauthorised access or damage to potential items, sites or places of Aboriginal heritage | SCEE-BS-HS-POL-0002 Environmental Policy 201047-HE-PER-0002 Excavation Permit. | Land access enquiries - heritage items not anticipated to be encountered at this project location If any items of possible indigenous significance are discovered during construction, work is to stop immediately and Project Manager to be contacted. Works will not recommence without the prior approval of the appropriate authority. Heritage trees to be marked and protected. | Major | Rare | 3 | M11 |  | Site First Aiders Site Medic Emergency Channel 39
Weather Conditions | Adverse / Inclement Weather - Strong Winds / Lightning Flooding | Loose or flying materials. Lightning Strikes. Floods. Personal Injury Property Damage Environmental Impact | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0011 Inclement Weather Management | Monitoring BOM Conducting pre -forecasted storm weather reports Tie - down for equipment and materials. Storm water run-off in to designated detention basins. Communicate weather conditions to supervisors as per weather front details. 30 / 30 rule lighting detected on track within 10 kms of project area. Secure all plant and machinery on firm stable higher ground. Work front inspection prior to re-commencement where event had the ability to significantly change the work environment, at direction of site superintendent | Major | Unlikely | 3 | M12 |  | Site First Aiders Site Medic Emergency Channel 39
Refuelling of mobile plant/equipment | Hydrocarbon spills | Hydrocarbon spill from mobile plant refuelling operations (including crane, telehandler, earthmoving equipment) entering environment and/or Collie River | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SWMS-201074-SE-060 Fuel Trailer Refuelling SCEE-BS-HS-WIN-0021 Hazardous Materials Handling and Storage | Ensure spill tray/mat is present whilst refuelling plant and equipment Ensure only authorised personnel refuel plant Ensure refuelling presonnel have read and signed onto SWMS-201074-SE-060 Fuel Trailer Refuelling Ensure any spills are controlled, contained and cleaned up promptly All spills, however small must be reported to the relevant environmental department on site | Major | Rare | 3 | M11 |  | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Operation of mobile plant / equipment | Uncontrolled movement of plant being unloaded | Rollover / Struck by plant falling from ramps Damage to environment due to hydrocarbon or chemical spills | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SM-GUI-0001 SCEE Loading and Unloading Guidance Note SCEE-BS-HS-SWM-0022 Loading and Unloading of Material Plant and Equipment on Site | Dedicated unloading area SWMS JHA Take 5 ROPS and FOPS where required Heavy duty rated loading ramps Exclusion zone large enough for the risk during loading / unloading. Use cones / barricading to prevent access Use spotter during loading / unloading Ensure tracks aligned with ramp Operator seatbelt/harness for plant that is not remote controlled Extra Spotter(s) where required in restricted areas Spill kits available CCCC procedures to be followed if hydrocarbon or chemical spill occurs | Severe | Unlikely | 4 | H17 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
Plant Operations / Adjacent to Bulk Earthworks | Work near earthwork mobile plant. | Interaction between construction personnel and earthworks/civil equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Windrows / Concrete Barriers to provide adequate separation and containment from earthwork mobile plant movements. No access into earthworks areas without Positive Communications between work groups. Restrict plant movements where access is required for entry into earthwork operations . | Severe | Rare | 4 | M13 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
Crane Operations | Failed lift/ Falling load Incorrect lifting equipment techniques/ swinging loads Incompetent/ unlicensed operators and dogmen/ riggers | Injury; Damage to plant and infrastructure Damage to environment due to hydrocarbon or chemical spills | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-0026 Crane Activity (High Risk) SCEE-BS-HS-SWM-0019 General Mobile Crane Work WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SYN-PRC-HSA-006 Synergy Lifting Operations Procedure | No load be lifted over any personnel; Tag lines to be used on all lifts Exclusion zones erected - Hard barricading with warning signs to be in place, only those involved in the works to enter; Laydown areas to be delineated with call up UHF Channel signs displayed at entry points Ensure level, stable ground for plant set up - crane pad design in place and adhered to; Experienced, competent, HRWL personnel to perform lifts; 'CN' class - Only nationally trained and accredited operators shall be authorised to use a Telehandler/IT Loader/Excavator with a jib attachment that is greater than 3 tonnes; Dogger/ Rigger to inspect lifting gear prior to use and ensure load is within lifting capacity of the equipment, check load chart, ensure load is secured correctly All lifting equipment to be quarterly tagged and registered on Lifting Gear Register; Lift study/plan above 75% of crane rated capacity; Crane inspection and certificates; Plant premobilisation check; Plant risk assessment; Daily plant prestart checks; Complete Prelift Checklist for each crane setup; Monitor wind conditions; Spill kits available and personnel trained in their use CCCC procedures to be followed if hydrocarbon or chemical spill occurs SWMS/ JSA CCCC procedures to be followed if hydrocarbon or chemical spill occurs SWMS/ JSA | Severe | Unlikely |  | H17 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
| Crane failure | Injury; Damage to plant and infrastructures | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-0026 Crane Activity (High Risk) SCEE-BS-HS-SWM-0019 General Mobile Crane Work WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SYN-PRC-HSA-006 Synergy Lifting Operations Procedure | Exclusion zones erected - Hard barricading with warning signs, only those involved in the task are to remain in the area; All cranes to be inspected for compliance before being sent to site; Annual Inspections / Crane Safe Servicing Inspections; Crane must be registered with WorkSafe; Complete Prelift Checklist for each crane setup; Plant premobilisation check; Plant risk assessment; Daily plant prestart checks; SWMS/ JSA | Catastrophic | Rare |  | H19 |  | Site First Aiders Site Medic Emergency Channel 39
| Crane rollover Crane Collision with infrastructure and other plant/ equipment | Injury; Damage to crane, equipment or infrastructure | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-0026 Crane Activity (High Risk) SCEE-BS-HS-SWM-0019 General Mobile Crane Work WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SYN-PRC-HSA-006 Synergy Lifting Operations Procedure | Compliance with load rating on crane; Use crane fitted with ROPS required by legislation or if required by task risk assessment; Crane must be fitted with an external load capacity indication light system; Set crane up on level surface, preferably utilising the sealed road/access way; Experienced personnel, competent, licensed; Inspect ground conditions for buried surfaces, recent excavations/backfill. Services Drawings if available; Ground conditions to be assessed, obtain geotechnical report where required; Confirm crane locations prior to lifts and ensure the operating radius does not cause any risk; Crane must be operated and maintained in accordance with the manufacturer's instructions; Annual Inspections / Crane Safe Servicing Inspections and Inspection report; Person(s) in control of lift dogman/rigger; Use spotter to guide and assist; Dogger/ Rigger to ensure load is within lifting capacity of the equipment; Crane pads to be used as per application; Complete Prelift Checklist prior to use; SWMS/ JSA | Catastrophic | Rare |  | H19 |  | Site First Aiders Site Medic Emergency Channel 39
| Operation of crane around or above personnel Load suspended over personnel Load coming in contact with personnel | Injury; | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-0026 Crane Activity (High Risk) SCEE-BS-HS-SWM-0019 General Mobile Crane Work WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SYN-PRC-HSA-006 Synergy Lifting Operations Procedure | No load be lifted over any personnel; Exclusion zones erected - only those involved in the works to enter; Experienced personnel, competent, licensed; Warning signs and barricading; Hand signal and line of sight/visual contact communication; UHF radios, Use spotter to guide and assist; Check wind conditions are safe; Certified and inspected lifting gear; Tag lines to be used; SWMS/ JSA; Take 5 | Severe | Unlikely |  | H17 |  | Site First Aiders Site Medic Emergency Channel 39
Working in EWP (Boom Lift) | Fall from heights | Injury; | C2761-WHS-MP-001 WHS Management Plan WHS-SWP-004 Working at Heights; WOP-REG-005 Working at Heights Equipment Register C2761-WHS-MP-002 Emergency Management Plan WHS-FM-022 HRW Rescue Plan (as required) | Keep limbs inside basket at all times; Wear fall arrest system and 100% hook up at all times (boom type EWP) Ensure EWP is on firm level ground; Underground services and infrastructure to be assessed to ensure that they do not compromise the stability of the EWP. Dropped Object Prevention - All equipment and tools shall be secured to prevent them falling from height, tool lanyards shall be used. Personnel to possess HRWL-EWP when using boom type EWP where height of EWP exceeds 11 metres; Verification of competency for operator; EWP premobilisation check prior to mobilisation; Ensure EWP is used in accordance with manufacturer's specifications and log books are available; Conduct daily prestart on EWP; Fall arrest equipment to be inspected before use and inspected/tagged quarterly; Working at Heights Equipment Register; Working at heights permit; Use spotter who holds HRWL-EWP - one spotter per machine; SWMS/ JSA; No shark hooks for use on EWP, triple action karabiners / anchor point attachments shall be used Approved working at heights rescue plan in place ; Wear and carry appropriate PPE | Major | Unlikely |  | M12 |  | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
| Falling tools/ dropped objects | Injury; | C2761-WHS-MP-001 WHS Management Plan WHS-SWP-004 Working at Heights; WOP-REG-005 Working at Heights Equipment Register C2761-WHS-MP-002 Emergency Management Plan WHS-FM-022 HRW Rescue Plan (as required) | Exclusion zone around machine and actively managed drop zone under basket Use of tool lanyards/bags Ensure EWP is on firm level ground; Personnel to possess HRWL-EWP when using boom type EWP where height of EWP exceeds 11 metres; Conduct daily prestart on EWP; Working at heights permit; Use spotter who holds HRWL-EWP - one spotter per machine; SWMS/ JSA; Wear and carry appropriate PPE | Moderate | Unlikely |  | M7
| Toppling over | Injury; Damage to environment due to hydrocarbon or chemical spills | C2761-WHS-MP-001 WHS Management Plan WHS-SWP-004 Working at Heights; WOP-REG-005 Working at Heights Equipment Register C2761-WHS-MP-002 Emergency Management Plan WHS-FM-022 HRW Rescue Plan (as required) | Wear fall arrest system and 100% hook up at all times (boom type EWP) Ensure EWP is on firm level ground; Periodical EWP maintenance checks to verify operation of safety cutouts Annual Inspection of machine Personnel to possess HRWL-EWP when using boom type EWP where height of EWP exceeds 11 metres; Verification of competency for operator; EWP premobilisation check prior to mobilisation; Ensure EWP is used in accordance with manufacturer's specifications and log books are available; Conduct daily prestart on EWP; Fall arrest equipment to be inspected before use and inspected/tagged quarterly; Working at Heights Equipment Register; Working at heights permit; Use spotter who holds HRWL-EWP - one spotter per machine; SWMS/ JSA; Site Emergency Response Team to be notified of workers working at height Underground Services and Infrastructure assesssed to ensure that they do not compromise the stability of the EWP. Approved working at heights rescue plan in place ; Wear and carry appropriate PPE Spill kits available CCCC procedures to be followed if hydrocarbon or chemical spill occurs | Major | Unlikely |  | M12
TOOLS & EQUIPMENT USE
Use of electrical powered plant & equipment | Electricity | Electrical shock | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SYN-STD-HAS-0006 Prohibited and Restricted Equipment Standard | Double adaptors/ three-pin (piggy back) and other domestic multi-plug power boards are not permitted, (office environment may utilise multi-plug boards that are individually switched) Electrical leads tested and tagged Electrical leads inspected before use All power boards fitted with residual current devices (RCDs). Non-portable 30 mA RCD shall be fitted in all switchboards All portable outlet devices must include over current protection & 30mA RCD All portable RCDs are to be tested before use Extension leads shall not be joined (Daisy chained) together SWMS JHA Take 5 | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 AS/NZS 3000 AS/NZS 3012
Use of High Pressure Water Equipment for exposing services | Stored energy | Injury to eye or skin cuts & abrasions Damage to flora/fauna natural habitats | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0021 Trenching and Excavating (High Risk) WOP-SWP-081 Excavation | Excavation Permit/inspection of area before task commencement Only experienced persons in handling of the equipment to carry out high pressure water jetting operations Water jet not to be pointed at workers PPE - safety glasses, face shield, hearing protection, safety boots and gloves Maintain minimum distance of 400mm between end of jet nozzle and subsoil or underground utilities Do not aim at underground utilities Max. 1500 PSI in or around underground utilities SWMS JHA Take 5 Check excavated areas for fauna before commencing work If fauna is identified as being trapped, contact a responsible person to determine appropriate removal measures Maintain good housekeeping practices | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Use of vibrating tools and equipment | Vibration | Injuries caused by vibration & manual handling Distress to fauna caused by vibration | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WEM-SWP-104 Noise, Dust and Vibration Management | Rotate tasks; Vibration resistant gloves; Scheduled maintenance & inspection of tooling; Manual handling technique awareness; Avoid excessive or unneccessary operations JHA Take 5 | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Working with ladders | Slip/ fall from ladder | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-0020 Portable Ladders WHS-SWP-004 Working at Heights; SYN-PRC-HAS-0010 Safe Work at Height Procedure | Fixed industrial single ladders are to be used for access only, no work to be carried out from these types of ladders; Only platform ladders with back bar to be used for any type of work; Inspect ladder before use and tagged quarterly; JHA Take 5; | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Working with mobile scaffold | Slip / fall from scaffold Scaffold collapse | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-0004 Scaffolding Safety | Ensure scaffold is built in accordance with manufactureres instructions; Ensure footings are firm (compacted), and stable prior to building mobile scaffold Underground Services and Infrastructure is assesssed to ensure that they so not compromise the stability of the Scaffold. Scaffold not to be constructed where there is a potential for ground slippage or errosion. All scaffolding must be erected by a person holding a High Risk Work Licence in Scaffolding; Scaffolding shall be inspected by competent person/Site Supervisor prior to use; SWMS/ JSA | [5 empty] | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Hot works Cutting Welding Grinding | Dust & Noise Metallic grinding shards Metal offcuts Discarded electrodes Discarded cutting discs | Injury Environmental contamination caused by hot work processes | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0015 Hot Work (High Risk) WOP-SWP-042 Hot Works SYN-PRC-FE-HSE-006 Hot Works Procedure | Shielding/containment of grinding operations from other works Screening of welding operations; Clean up work area as you go Hot work permit; Only qualified personnel to use hot work apparatus; JHA, Take 5; Wear double eye protection when cutting and grinding; Wear ear protection/muffs plugs and protective gloves Dust suppression Use barriers around hot work and grinding areas Collect grinding shards, metal offcuts, and waste materials Provide designated bins for waste materials | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Welding flash causing burns to body parts | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0015 Hot Work (High Risk) WOP-SWP-042 Hot Works SYN-PRC-FE-HSE-006 Hot Works Procedure | Only qualified and trained personnel to use hot work apparatus; Check equipment before use; Exclusion zone, barricading, welding screens; JHA, Take 5; Welder to wear welding helmet, and welding gloves, safety glasses with side shields spotter/fire watch; | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Electric Shock | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0015 Hot Work (High Risk) WOP-SWP-042 Hot Works SYN-PRC-FE-HSE-006 Hot Works Procedure | Welders to have VRD Fitted; Ensure gloves and PPE are dry; Ensure return lead is positioned as close to the work as possible; Handpiece to be held in hand when removing stubs and changing rods for MMAW ; JHA, Take 5; | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Fire/ explosion from this type of work being performed | Destruction of property; Destruction of flora and fauna; Injury or death to personnel or public | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0015 Hot Work (High Risk) WOP-SWP-042 Hot Works SYN-PRC-FE-HSE-006 Hot Works Procedure | Hot Works Permit; Maintain 10m exclusion zones from Hydrocarbon or flammable materials storage areas; JHA Take 5; Monitoring of DFES Fire Alerts; Daily fire danger rating to be communicated by Supervisor at pre-starts; Observe total fire bans unless exemption is granted and supported by risk assessment; Fire protection equipment on mobile plant and vehicles (fire extinguishers and/or knapsacks); Inspection & servicing of fire extinguishers; Equipment inspected before use; Conduct a pre-work fauna inspection Conduct a post-work inspection to ensure no smouldering materials Clear vegetation around hot work zones Ensure site has firebreaks | Major | Unlikely | 3 | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 | Project Manager | Ongoing
MOBILE PLANT OPERATION
Operation of mobile plant / equipment | Plant / equipment not maintained | Equipment failure Practical Completion (PC) date not met due to plant unavailability | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Service and maintain plant and equipment according to manufacturer's service and maintenance schedule; Maintenance logs maintained; Only qualified and competent persons to carry out the repairs, services and inspections; SWMS JHA Take 5 | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Plant in the Workplace
Operation of mobile plant / equipment | Hydraulic / oil spill | Damage to flora / fauna Destruction of flora/fauna habitats | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Equipment pre-start; Spill kits; Personnel trained to use spill kits; Project Induction; SWMS JHA Take 5; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Plant in the Workplace
Operation of mobile plant / equipment | Work in proximity to mobile plant | Personnel and / or other plant struck by mobile plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Traffic Management Plan; Controlled exclusion zones established on site; (50/20/10) approach process for personnel and vehicles entering ito the work area of mobile plant; Positive communication to be established for any interaction between personnel and / or mobile equipment; Designated Pedestrian Walkways, segregated with fencing/crowd control barricade in high traffic areas; Licensed, qualified, competent operators; SWMS JHA Take 5; | Severe | Unlikely | 4 | H17 |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Plant in the Workplace
EARTHWORKS
Installation of underground services. | Underground services | Contact with underground utility (e.g. HP water, electricity) Damage to utility / equipment Injury or fatality Schedule delays from redesign | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-Trenching and Excavation (High Risk) WOP-SWP-081 Excavation 201074-SE-0004 Excavation Permit SYN-PRC-FE-HSE-014 Excavation and Penetration Works Procedure | Excavation Permit; Licensed plant operators; Project Manager to determine whether utility owner permits are required (e.g. WP Vicinity Access permit), at pre-planning stage of every job; Pre-job JHA & SWMS (inc. MADs, potholing where appropriate); Pothole utilities within 2m of any excavation and at every entry and exit point for drilling; Use non-destructive digging tools only (e.g. shovel, prodder, vacuum excavation); Maximum Water Jetting to 1500psi (100 bar) to avoid damaging services; Work Scheduling and Planning before job is undertaken; Protect the utility once exposed; Water main to be supported at every connection or joint; Commence only when plan to execute work is clear & all services have been located; Maintain Minimum Approach Distances (MADs) (300mm min. from underground utilities) (increase distance for HP / HV services per utility owner requirements); No trenches or excavated holes left open exposing services; SWMS JHA Take 5; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Working near overhead services | Overhead services | Contact with live power sources resulting in electrocution, electric shock, arc flash or burns Damage to service / network outages | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-Trenching and Excavation (High Risk) WOP-SWP-081 Excavation 201074-SE-0004 Excavation Permit SYN-PRC-FE-HSE-014 Excavation and Penetration Works Procedure | Excavation Permit; Eliminate unloading zones under neath overhead services; Placement of overhead protection warning / barriers to MADs overhead services; SWMS JHA Take 5; HV Vicinity Permit (Western Power); Pre-job JHA incorporating any overhead hazards; Maintain MADs; Spotter mandatory; Licenced, qualified and competent operators; | Catastrophic | Rare | 5 | H19 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Vegetation Management | Land / tree disturbance | Tree damage, death or destabilisation | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan C2761-WEM-MP-001 Environmental Management Plan SCEE-BS-HS-WIN-Trenching and Excavation (High Risk) WOP-SWP-081 Excavation 201074-SE-0004 Excavation Permit SYN-PRC-FE-HSE-014 Excavation and Penetration Works Procedure | Exclusion Zone around trees; SWMS JHA Take 5; Avoid disturbance wherever possible; | Moderate | Unlikely | 2 | M7
Excavations and Trenches | Open excavation | Injury to personnel and equipment damage by falling into excavations Collapse of trench, falling plant or personnel Damage to nearby fences / structures Collapse of road | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-Trenching and Excavation (High Risk) WOP-SWP-081 Excavation 201074-SE-0004 Excavation Permit SYN-PRC-FE-HSE-014 Excavation and Penetration Works Procedure | Excavation Permit; Barricading and signage; Excavations to be closed as soon as possible; Check stability of buildings, roads or structures that may be affected by the excavation before starting work; Do not place loads near edge of the excavations where there is a potential of load falling into excavation; Barricade to be set back 500mm from edge of trench; Stock pile soil minimum 1m away from side of trench; Redesign alignment to move away from fence line; If personnel are required to enter excavation: - Excavation planned to be < 1.5m where possible; - No tools/equipment left unattended within 1m of excavation edge where is risk of falling onto people below; - Examination of excavation integrity by a competent person before entry; - Any excavation that is over 1.5m must have either shoring, battering of the side of the trenches or/and trench walls stepped down; SWMS JHA Take 5 | Major | Unlikely | 3 | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Flora Fauna Interaction | Flora & Fauna | Trapped fauna resulting in injury or death to fauna | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan C2761-WEM-MP-001 Environmental Management Plan SCEE-BS-HS-WIN-Trenching and Excavation (High Risk) WOP-SWP-081 Excavation 201074-SE-0004 Excavation Permit SYN-PRC-FE-HSE-014 Excavation and Penetration Works Procedure | Contact Principal local authorities / qualified competent fauna handler to remove injured fauna; Inspect trenches/ excavations for trapped fauna prior to starting work; Where excavations open out of hours Fauna ramps every 15 meters; Backfill as soon as practicable; Any fauna sightings to be added to the SCEE Fauna Interaction Register and reported to Synergy SHEQ team. Project to report any injury caused to fauna to Synergy SHEQ team; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
HEALTH & HYGIENE
Outdoors work | UV radiation exposure Exposure to extreme temperature (heat) | Heat-related illness Skin cancers | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Air-conditioning fitted to vehicles, can be used as refuge; Adequate provision of water; Portable shade made available; PPE - sunscreen, UV rated long clothing, sunglasses, hard hat brim; Hydration monitoring during warm months; JHA Take 5; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Hazardous manual tasks | Sprains and strains | Musculoskeletal injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0006 Manual Handling WHS-SWP-801 Manual Handling | Use mechanical aids and additional manpower for heavy loads; Keep hands/feet/fingers clear of line of fire at all times; Clear and accessible work area allowing for safe movement of people, equipment and materials; Manual handling induction site induction; Employ correct manual handling techniques at all times; Warm up/stretching activities; Raise awareness at site induction and toolbox meeting toolbox meeting/ daily prestart; JHA, Take 5; Regular checks on PPE; Wear appropriate PPE e.g. Safety boots, gloves, Safety glasses etc. | Major | Unlikely | 3 | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Hazardous Manual Tasks
| Cuts, Abrasions & Lacerations | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0006 Manual Handling WHS-SWP-801 Manual Handling | Keep hands/feet/fingers clear of line of fire at all times; Clear and accessible work area allowing for safe movement of people, equipment and materials; Manual handling component of site induction; correct manual handling techniques; Raise awareness at toolbox meeting/ daily prestart; JHA, Take 5; Regular checks on PPE; Wear appropriate PPE e.g. Safety boots, gloves, Safety glasses etc. | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Crush-pinch points | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-0006 Manual Handling WHS-SWP-801 Manual Handling | Keep hands/feet/fingers clear of line of fire at all times; Clear and accessible work area allowing for safe movement of people, equipment and materials; Manual handling component of site induction; Correct manual handling techniques; Raise awareness at toolbox meeting/ daily prestart; JHA, Take 5; Regular checks on PPE; Wear appropriate PPE e.g. Safety boots, gloves, Safety glasses etc. | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Dangerous Goods & Hazardous Chemicals - Storage, Handling and Transport | Hazardous materials contacting workers or released to environment | Adverse impact on worker health Adverse environmental impact, contamination of soil, groundwater, or transfer of contaminated material to river following rain event | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan C2761-WEM-MP-001 Environmental Management Plan SCEE-BS-HS-WIN-0021 Hazardous Materials Handling and Storage (High Risk) 201074-SE-PLN-002 Emergency Response Plan (incorporating DG Storage Licence Requirements) | Correct storage facilities; Haz chem cabinets contain bunds with excess capacity to contain all chemicals; All decanted chemicals are to be appropriately labelled and stored in containers that are fit for use; Spill kit; Report all spill incidents immediately; WOP-FM-001 Daily housekeeping inspection; WEM-FM-002 Weekly Environmental inspection; WOP-FM-002 Monthly site inspection; Housekeeping; Align with SDS requirements for storage, use, PPE and cleanup; Hazardous Chemicals Register (Chem Alert); Hazardous Chemicals Risk Assessments (no 'red-rated' chemicals in use); Quantities of hazardous chemicals are classified as 'minor storage'; Hand washing facilities available; First aid kit available; JHA, Take 5 | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Hazardous Chemicals in the Workplace WA Dangerous Goods Safety (General) Regulations 2007 WA Dangerous Goods Safety Act 2004
Site Work | Noise (environmental) | Noise, light and vibration emissions during construction works. Nuisance to Stakeholders | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-PRO-009 Noise Control and Hearing Protection WEM-SWP-104 Noise, Dust and Vibration Management | Approved normal construction hours within Synergy Operation Hours; Hearing protection in proximity to operating plant; Task rotation; JHA/Take 5; | Moderate | Unlikely | 2 | M7 |  | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Noise and Preventing Hearing Loss at Work
Site Work | Extreme wind or environmental work conditions | Injury from windborne dust, loose objects, | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WEM-SWP-104 Noise, Dust and Vibration Management | Supervisors and SHEQ to review and monitor BoM for expected extreme weather and wind conditions; Loose materials to be secured to prevent flying particles or objects; When storm force wind levels present risk of injury to workers construction manager shall identify alternative work areas shall be identified, i.e. in workshops, offices, buildings, switchyards; AS/NZS 1336 Eye and face protection to be worn. This may include over goggles if works are to proceed in work environments where flying particles cannot be controlled by isolation or engineering controls; JHA, TAke 5; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Provision of Medic services | exposure to pathogens | infection of personnel through contact with infected bodily fluids or airborne pathogen | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan 201074-SM-PRO-002 Medical Services and First Aid | Qualified and competent personnel; Processes used by medic to follow established best practice in disease prevention; Medical room equipped with disinfectant ; Regular cleaning of medical room and equipment; Use of disposable, single use supplies; PPE - disposable surgical masks, examination gloves, disposable smock; | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Site Work | Fatigue | Event and/or injury resulting from worker fatigue | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan Mental Health Policy WHS-POL-003 WHR-POL-001 Fitness for Work Policy; WHR-PR- 001 Fitness For Work Procedure SCEE-BS-HS-PRO-0025 Fatigue Management SCEE-OP-OP-TEM-0021 Worker Fatigue Checklist | Mandatory rest period of 10 hours before next shift; Rostered break amongst site personnel where applicable; Task rotation where required; Site Supervisor to monitor and ensure the workers stay hydrated; Site Supervisor to observe for symptoms of fatigue; Raise awareness on fatigue at induction and toolbox meetings & daily prestart meeting; Fatigue management covered in JHA where relevant; Fatigue Checklist; | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Site Work | Mental Health | Health issues | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan Mental Health Policy WHS-POL-003 | Mental Health First Aider available; Employee Assistance Program (EAP) available; Site induction cover mental health; Site Supervisor to observe symptoms of fatigue/Stress /Burnout; Management ensures structure of shifts and rosters are compliant withs site management plan, correct shift rotations etc; Peer on peer monitoring; | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
Site Work | Psychosocial Risk | Illness; Injury; Distress | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan Mental Health Policy WHS-POL-003 | Mental Health First Aider available; Employee Assistance Program (EAP) available; Site induction to cover mental health; Maintain Regular Communication; Well-being checks; Provide opportunity for skills development; Ensure workers know where they can get help from; Supportive leadership skills (open door); Promote positivity; Foster a culture of transparency, openness, respect and equity; Provide workers with ways to report issues and raise concerns; Provide positive feedback and acknowledgement; Ensure communication systems and emergency procedures are developed and in place; Reward and Recognition program in place; Zero tolerance of aggression towards workers; | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
GENERAL
Site Work | Simultaneous Operations (e.g. work around other trades) | Impact to other works | SIMOPS | Daily communication / consultation with stakeholders; Communication between work groups; SCEE Project Manager to resolve priority access if required; JHA, Take 5; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Site Work | COVID-19 | Contraction of COVID-19 from other workers | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Comply with Mandated Government Procedures; Provision of hand wash facilities / sanitiser; Only trained personnel to conduct drug and alcohol testing; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Site Work | Smoking | Personnel contracting disease from exposure to passive smoke | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-POL-005 Non Smoking Policy | Smoking in designated smoking areas only; No smoking or vaping on wider construction site; | Minor | Unlikely | 1 | L2 |  | Site First Aiders Site Medic Emergency Channel 39
WASTE MANAGEMENT
Waste Disposal | Site waste entering waste stream in uncontrolled manner | Wastage of recyclable goods, contamination of waste streams, electricity consumption | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-003 Waste Management Plan | Project Induction; Segregated Waste Bins; All waste removed from site; Scrap metal, PVC, general and recycling skip bin(s) to be made available; | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| incorrect disposal of site generated controlled waste | Controlled waste entering local environment, breach of legislation | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-003 Waste Management Plan | Segregation and labelling of controlled waste; Disposal of waste using licenced controlled waste contractor Ensure personnel are trained on waste disposal procedures | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
EMERGENCY
Emergency Incident | Fire, explosion, medical emergency, utility strike, Hazchem spill / release, severe weather, bomb threat, intruder | Personal injury or fatality | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan | Emergency Management Plan; Trained First Aiders; Site medic and medical room; Scheduled servicing and inspection of emergency and firefighting equipment; First aid kits available; Natural ventilation for fuel and Hazchem storage areas; Emergency WA RSS feed monitored by SHEQ department; Drills / testing frequency as per Emergency Drill Schedule. Formal effectiveness review following each evacuation (drill or actual); Water cart with cannon to be maintained, one on site at all times | Moderate | Unlikely | 2 | M7 |  | Site First Aiders Site Medic Emergency Channel 39
BATTERY TRANSPORT
Battery Recieval | Battery transport to unload point | Transport rollover caused by uneven ground and / or soft ground Battery Fire caused by transport rollover Transport interaction with other plant and / or personnel Biosecusirty breach (e.g. foreign flora or fauna present on battery) | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan CargoWorks TMP - Synergy Collie BESS Project CBESS Materials management Plan - 201074-SE-PLN-0001 | Traffic Management Plan to be followed Regular checks on road conditions Weather checks for future transport arrivals Batteries to be checked for foreign fauna at ship loadout point Consult with Synergy if any foreign flora or fauna is detected on shipments. | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
BATTERY PLACEMENT
Crawler Crane Assembly Area Inspection | Vehicular & pedestrian traffic in and around area | Personnel and / or other plant struck by mobile plant Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan TEM-069 General Crane Services SWM - Crawler Crane Assembly / Dismantle | CBESS project site induction for all contractors. Traffic Management Plan to be utilised. Site personnel will establish and monitor an exclusion zone for each stage of the crawler crane's erection. While Vehicles are operating, Spotters are in place, reversing beacons/alarms & flashing lights in operation. Safety signs are to be displayed at each approach to the erection area. Barriers installed around Mobile Crane outriggers Clean work area before commencing work. Stack and/or store materials and equipment in lay-down areas provided. Use gloves at all times | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
Assembly / Dissasembly of Crawler Crane | Unloading Crane components from Transport | Injury or damage from the movement of plant & equipment Failure of crane while moving components Falls from height while accessing components Pinch points between crane components | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan TEM-069 General Crane Services SWM - Crawler Crane Assembly / Dismantle | Ensure work area is delineated Ensure positive communication with the plant operator when moving around the plant. Transport must only be operated/driven by approved, suitably ticketed/licensed personnel to be nominated by General Crane Services (WA). All cranes to be inspected by competent person before operation Platform ladders with back bars to be utilised All movements of the crane are to be communicated to all personnel involved and conducted by a designated person. Ensure personnel keep clear of all moving areas of the crane whilst the powered operations are taking place | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Assembling Crane | Equipment failure caused by untrained assembly personnel Pinch points between crane components Falling Objects Component Rollover Collision with other plant Failure of crane while moving components into place Personnel / Vehicle interactions with crane while moving components Failure of crane components during operational limit testing Fluid loss / Ground contamination causing environmental impact Inclement weather - Lightning / Storms while Assembling Sunlight / Dehydration | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan TEM-069 General Crane Services SWM - Crawler Crane Assembly / Dismantle SCEE-BS-HS-WIN-0026 Crane Activity (High Risk) SCEE-BS-HS-SWM-0019 General Mobile Crane Work WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SYN-PRC-HSA-006 Synergy Lifting Operations Procedure | Develop a plan identifying the weights of components, weight distribution, crane standing in position, outrigger locations, centre of rotation, radius line at pick up, radius line at placement, tail-swing radius line, clearances for mobile cranes, and equipment to be used. All movements of cranes are to be communicated to all personnel involved and conducted by a designated person. Ensure personnel keep clear of all moving areas of the crane whilst powered operations are taking place Exclusion zones /Drop Zones to be utlised when assembling. All loads must be slung by a competent dogger/rigger. Ensure all loads are stable on a level surface before releasing them and unlashing them from the crane so materials do not fall over. Complete visual inspection of crane components, including rope terminations, to be completed prior to commencing test lift and results recorded in commission paperwork. Ensure adequate spill kits are available Rigging supervisor to monitor load indicators during all stages of load tests. Maximum rated capacity of crane not to be exceeded at any time. Ensure the crane is not erected during any pending electrical or severe storm. Ensure the crane is not to be erected if wind speed exceeds 10m/s and/or rain. Ensure to obtain weather updates prior to testing commencement. Ensure regular breaks and regular fluid intake are upkept | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Crawler Crane Operations | Lifting and landing Battery Packs from transport | Crane rollover due to unsuitable operation pad Equipment failure during operation Personnel and / or other plant struck by mobile plant Battery dropped while unloading resulting in electrolyte / coolant discharge to environment Battery fire whilst on transport or when landed | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan SCEE-BS-HS-WIN-0026 Crane Activity (High Risk) SCEE-BS-HS-SWM-0019 General Mobile Crane Work WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SYN-PRC-HSA-006 Synergy Lifting Operations Procedure | No load be lifted over any personnel; Tag lines to be used on all lifts Exclusion zones erected - Hard barricading with warning signs to be in place, only those involved in the works to enter; Laydown areas to be delineated with call up UHF Channel signs displayed at entry points Ensure level, stable ground for plant set up - crane pad design in place and adhered to; Experienced, competent, HRWL personnel to perform lifts; Only nationally trained and accredited operators Dogger/ Rigger to inspect lifting gear prior to use and ensure load is within lifting capacity of the equipment, check load chart, ensure load is secured correctly All lifting equipment to be quarterly tagged and registered on Lifting Gear Register; Lift study/plan to be utilised Crane inspection and certificates; Plant premobilisation check; Plant risk assessment; Daily plant prestart checks; Complete Prelift Checklist for crane setup; Monitor wind conditions; Spill kits to be available to contain and control any chemical spill SWMS/ JSA | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Landing Battery Packs | Personnel working on and around battery pad footings | Slips / Trips / Rolled Ankles due to open conduit box outs in battery pads Fauna entrapment in box outs Interaction with entrapped fauna | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan | Formply covers to be fabricated to cover open box outs Excavated areas to be checked for fauna before works commence Good housekeeping practices, removal of equipment and materials not required out of the work area Contact the responsible person if fauna is identified as being trapped and implement appropriate removal measures based on the situation.
WORK In EARLY MORNING/NIGHT
Nightshift Works | Terminations | Poor lighting resulting in trips or falls | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan 201074-SE-PLN-0002 CBESS Emergency Response Plan | Provision of temporary lighting towers Use of headlamps if required Limniting works to inside switchrooms, termination work where possible No high risk work, EWP work Provision of site medic for night works Transport to and from site by bus | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
|  | Oil spills from diesel lighting towers | SYN-STD-ENV-0001 - Synergy Environmental & Heritage Management 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Project should use solar lighting tower. (Were Pracitable) Refueling to be completed on dayshift, if required. Diesel lighting towers to be self bunded. | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
|  | Unwanted fauna within workarea | SYN-STD-ENV-0001 - Synergy Environmental & Heritage Management 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Lighting towers to be directed downwards (Angle low) and focused on the work area Switch room doors to be kept closed when not in use. Office and crib room doors to be kept closed as to reduce office and crib lighting. Office and crib rooms not in use shall have lights turned off. (Inlcuding stores) | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39

## Civil & UG Services
Register Type | Project Risk Register
Project(s) | CBESS BOP
Approved by
Task / Activity | Hazard | Risk (un-wanted event) | Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
Installation of Underground Services
Use of laser level | Damage to eyesight | Eye injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Elimination Never look directly into the laser beam or point the beam into the eyes of others. Engineering The maximum radiant power output of laser is less than 5mW; Set the laser at a height that prevents the beam from shining directly into others’ eyes; Administrative Train personnel to use the equipment; Do not remove any warning signs from the laser Inform all nearby crews of operations about to take place. | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Noise, dust and vibration from plant and equipment operations | Excessive noise, dust and vibration from construction works - earthwork, excavation, compaction, plant movement, stockpiling etc. | Air pollution affecting the health of flora / fauna and people (exposure injuries); Complaints on excessive noise, vibration and pollution; Legal non-compliance | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WEM-MP-001 Environmental Management Plan WEM-SWP-104 Noise, Dust and Vibration Management | Isolation Exposed surface to be minimised Engineering Use watercart if dust is excessive; Construction equipment selected, operated and maintained to minimise noise impacts and where necessary fitted with noise supressing device; Administrative Implement and adhere to Environmental Management Plan; Work within designated working hours; Provide respite periods for high noise generating activities; Strenuous activities shall be rotated between workgroup team members where required and feasible; Regular maintenance of plant; Plant premobilisation checks; Plant risk assessments; Daily plant prestart checks; Awareness training will be provided during the site induction; Conduct weekly environmental inspections Community liaison with stakeholders through notifications where required; JSA PPE Wear and/or carry correct and required PPE as signposted (dusk masks, ear plugs, ear muffs); Class 5 ear plugs and hearing protection shall be used as a minimum | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Noise and Preventing Hearing Loss at Work
Use of Franna/ Tele/ Crane/Excavator for Loading/Unloading | Failed lift, Falling load/ equipment rollover, Incorrect lifting equipment/techniques, Swinging loads, collision with other plant/equipment Incompetent/unlicensed operators, dogmen or riggers. | Injury, Damage to plant and infrastructures. | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SCEE-BS-HS-WIN-0026 Crane Operations (High Risk) SCEE-BS-HS-WIN-0027 Forklift Telehandler (High Risk) SCEE-BS-HS-PRO-0027 5 Star Commitment | Elimination No load to be lifted over any personnel at any time. Engineering Follow load rating on plant, Use equipment fitted with ROPS required by legislation or if required by task risk assessment, Crane must be fitted with an external load capacity indication light system, Set laydown area on level surface. Ground conditions and underground services/ infrastructure to be surveyed/ assessed to ensure that they do not compromise the cranes stability Underground services and infrastructure surveyed/assessed to ensure that they are not compromised by the crane set up. Isolation Exclusion zones erected - delineation/barricading with warning signs to be in place, only personnel involved in the lift/works be allowed to enter, Laydown areas to be delineated with call up UHF Channel signs displayed at entry points. Administrative Only licensed, ticketed, VOC'd and experienced personnel, 'CN' class - Only nationally trained and accredited operators shall be authorised to use a Telehandler/IT Loader with a jib attachment that is greater than 3 tonnes, Dogman or rigger to inspect lifting gear prior to use and ensure load is within lifting capacity of the lifting equipment, check load chart and ensure load is correctly slung and secured (With Tag line), All lifting equipment to be quarterly tagged and registered on Lifting Gear Register, Lift study/plan below 75% of crane rated capacity, Crane inspection and certificates, Plant premobilisation check, Plant risk assessment, Daily plant prestart checks, Complete Prelift Checklist for each crane setup, Loading/ Unloading Checklist to be completed for all loading & unloading of deliveries Weight of all crane lifts are known and calculations completed prior to the selection of rigging equipment. Monitor wind conditions SWMS/JSA | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
Use of Telehandler to move and place culverts and steelwork | Failed lift, Falling load/ equipment rollover, Incorrect lifting equipment/techniques, Swinging loads, collision with other plant/equipment Incompetent/unlicensed operators, dogmen or riggers. | Injury, Damage to plant and infrastructures. | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SCEE-BS-HS-WIN-0026 Crane Operations (High Risk) SCEE-BS-HS-WIN-0027 Forklift Telehandler (High Risk) SCEE-BS-HS-PRO-0027 5 Star Commitment | Engineering Ensure level, stable ground for plant set up - stable surface to be verified by compaction test; All lifting equipment has been inspected on arrival to confirm it has been tested and certified by the manufacturer or a testing authority accredited by NATA; Ensure use of positive closure fittings (e.g. shackles, hooks, etc) to prevent detachment from load while lifting; Ensure task rotation and regular breaks for operators Administrative Trained, competent HRWL personnel to perform lifting activities (Craneage & Dogging/Rigging); 'CN' class (for non-slewing telehandler) or C2 (for slewing) - Only nationally trained and accredited operators shall be authorised to use a Telehandler/IT Loader/Excavator, fitted with a jib attachment that combined have a capacity of greater than 3 tonnes; Dogger/ Rigger to inspect lifting gear prior to use and ensure load is within lifting capacity of the equipment, check load chart, ensure load is secured correctly; All lifting equipment to be quarterly tagged and registered on Lifting Gear Register; Lift study/plan developed where lifting above 75% of crane rated capacity or where lifts classed as medium or critical; Crane inspection and certificates completed and available on site; Plant risk assessment available in telehandler; Daily plant prestart checks; Complete Prelift Checklist daily; Monitor wind conditions at all times, where necessary lifting activities to cease; SWMS/ JSA | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
| Dropped Loads during lifting and/or transport | Injury, Damage to plant and infrastructures. | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SCEE-BS-HS-WIN-0026 Crane Operations (High Risk) SCEE-BS-HS-WIN-0027 Forklift Telehandler (High Risk) SCEE-BS-HS-PRO-0027 5 Star Commitment | Elimination No load be lifted over personnel; Isolation Exclusion zones erected - Hard barricading with warning signs to be in place,only those involved in the works to enter; Dogmen/riggers to guide loads using tag lines; Dual taglines to be used, where necessary, when landing culverts into trench to control the load - dogman in trench and dogman above trench; Personnel shall ONLY touch a suspended load to move into final position, ensuring the load is as close to the ground as possible Engineering Rubber magnetic strips to be placed on fork tynes prior to transporting culverts from laydown to work area | Major | Unlikely |  | Unlikely
| Telehandler Failure | Injury, Damage to plant and infrastructures. | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SCEE-BS-HS-WIN-0026 Crane Operations (High Risk) SCEE-BS-HS-WIN-0027 Forklift Telehandler (High Risk) SCEE-BS-HS-PRO-0027 5 Star Commitment | Elimination Equipment which is not deemed fit for purpose during onboarding inspections shall not be used until approved for site; Equipment which is not deemed fit for purpose during daily prestart inspections shall not be used until defects are rectified Administrative All equipment/plant to be inspected for compliance before being sent to site; Annual Inspections / Crane Safe Servicing Inspections where applicable; Telehandler must be registered with Worksafe (where being used as a crane); Operator to complete Prelift Checklist daily; Plant risk assessment; Daily plant prestart inspection | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Working/ transport of culverts in the vicinity of other work crews/ unauthorised personnel in area | Injury, | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SCEE-BS-HS-WIN-0026 Crane Operations (High Risk) SCEE-BS-HS-WIN-0027 Forklift Telehandler (High Risk) SCEE-BS-HS-PRO-0027 5 Star Commitment | Isolation Exclusion zones erected - Hard barricading (around BESS) with warning signs to be in place, only those involved in culvert crew to enter culvert installation work area; Delineation via hard barricading between culvert work crew and earthworks crew when working within the same BESS work area; Movement of culverts from laydown to BESS work areas shall be staggered to ensure minimal interaction with culvert delivery crew; Movement of culverts from laydown area to work area shall remain in barricaded/ cone delineated areas; Administrative Contractor Culvert Work area call up UHF Channel signs displayed at entry points; Gate Call up for culvert movements to be numbered and signposted; Telehandler transporting culverts shall have right of way at all times - to be reiterated at prestart meetings; Traffic Movement Plan in place and adhered to | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Poor Manual Handling/ pinch points | Injury, | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-022 Lifting equipment WOP-SWP-012 Mobile Crane SCEE-BS-HS-WIN-0026 Crane Operations (High Risk) SCEE-BS-HS-WIN-0027 Forklift Telehandler (High Risk) SCEE-BS-HS-PRO-0027 5 Star Commitment | Elimination Keep clear of line of fire at all times; Substitution Use mechanical aids and/or additional manpower for heavy loads; Engineering Packers to be taped to previous culvert prior to dropping in following culvert; Administrative Employ correct manual handling techniques at all times; Clear and accessible work area allowing for safe movement of people, equipment and materials; JSA; Take 5; Regular checks on PPE PPE Wear appropriate PPE e.g. Safety boots, gloves, Safety glasses etc. | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Hazardous Manual Tasks
Use of Mobile Plant | Faulty plant | Injury; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan Safe work procedures on various plant Plant & Equipment Register | Engineering ROPS, lights, beacons, radios as per site requirements; Administrative Only operators with correct tickets and in date VOCs to complete daily plant prestart; Plant premobilisation check prior to use on site; Plant risk assessment; Regular maintenance of plant; Establish Plant & Equipment Register; Measuring and testing equipment are calibrated; Safe work procedures on various plant | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Plant in the Workplace
| Collision with or reversing into personnel/ other plant/ vehicle | Injury; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Isolation Exclusion zone using Flagging/ hard barricading/ windrows Engineering ROPS, lights, beacons, radios as per site requirements Administrative Competent, licensed/ticketed, operators; Daily prestart check of plant; Hand signal and line of sight/visual contact communication; Positive communication at all times; Communication of all VMP changes in site notices; UHF radios to be used in work areas; Use spotter to guide and assist; SWMS/JSA; Drive to conditions at all times; Adhere to Traffic Management Plan/Vehicle Movement Plan PPE Ground personnel to wear appropriate PPE i.e. Hi vis clothing, hard hat, Safety glasses, Safety boots | Severe | Unlikely |  | H17 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Toppling over/ Rollover | Injury; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Isolation Delineation of Plant operations in place via barricading/ windrows etc Plant shall not operator Engineering Follow load rating on plant; Ground conditions to be level and smooth as practicable at all times free of obstructions Administrative Competent, licensed, operators; Regular maintenance of plant; Daily prestart check of plant; Hand signal and line of sight/visual contact communication; Use spotter to guide and assist where needed; Drive to conditions at all times; SWMS/ JSA; Adhere to Traffic Management Plan/ Vehicle Movement Plans | Severe | Unlikely |  | H17 |  | Site First Aiders Site Medic Emergency Channel 39
| Incompetent operator | Injury; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Administration Competent, licensed/ticketed, operators; Operator to be in control of plant at all times; Operator shall only commence operating plant after instruction to do so by supervisor; Operator’s manual available in plant for reference; Safe work procedures on various plant made available to operators | Severe | Rare |  | M13 |  | Site First Aiders Site Medic Emergency Channel 39
| Falling load | Injury; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Isolation Exclusion zone using Flagging/ hard barricading/ windrows around work area Do not lift or suspend load over any person Engineering Use plant fitted with FOPS required by legislation or if required by task risk assessment; Administrative Competent, licensed, operators; Load to be slung by Dogman/rigger, Drive to conditions at all times; Warning signs; Hand signal and line of sight/visual contact communication; UHF radios for positive communications; Use spotter to guide and assist; SWMS/JSA; PPE Wear appropriate PPE e.g. hard hat | Severe | Rare |  | M13 |  | Site First Aiders Site Medic Emergency Channel 39
| Plant on fire | Injury; Damage to plant Damage to personnel / flora / fauna by ingestion of toxic gases (smoke) | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Administrative Fire extinguisher on plant; Regular maintenance of plant; Plant premobilisation check prior to use on site; Plant risk assessment; Daily prestart check of plant | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
| Slip, trip or fall while using plant or in vicinity of plant | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Isolation Remove any objects that may obstruct personnel E.g. build-up of mud on steps. Engineering Ground conditions to be level and smooth as practicable at all times; Remove or stack neatly in a safe location all unwanted material from area Administration Climb in and out of cab and not jump down from the cab; Always maintain 3 points of contact when climbing; Maintain good housekeeping; SWMS/JSA; Take 5 PPE Wear correct PPE | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
| Hydrocarbon release to environment | Hydrocarbon spill from mobile plant (including crane, telehandler, earthmoving equipment) entering environment and/or Collie River | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan SCEE-BS-HS-WIN-0021 Hazardous Materials Handling and Storage | Spill kit, on plant where practicable; Regular maintenance of plant; Plant premobilisation check prior to use on site; Plant risk assessment; Daily prestart check of plant; Should a hydraulic leak develop, stop using the plant as soon as safe to do so and remove from service; Use of absorbent pads/sausages if required; with personnel trained in their use. Ensure proper disposal of contaminated cleanup materials. | Moderate | Unlikely |  | M7 |  | Notification of event to Synergy Enviromnental Representative as soon as possible
| Excessive noise & vibration & emission | Fauna disturbance; Public nuisance & complaints; Health risk to personnel; Structural damage to buildings | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Substitution Use alternative plant where necessary Engineering Adjust the compaction frequency of compaction equipment to reduce vibration, use plant as designed and intended plant manufacturer. Administrative Regular inspection and maintenance of plant; Work within designated working hours; Plant risk assessment; Daily prestart check of plant PPE Workers to wear ear plugs when working close noisy equipment | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39
Excavation | Damage to existing services | Damage to services; Injury; | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation; WOP-SWP-051 Working near Underground and Overhead Services | Administrative Obtain current services drawings from management team/ BYDA Review and understand the detailed services drawings; Locate services with cable locator and potholing/Vac truck by SCEE Use spotters when required; Excavation Permit approved & in place; Personnel trained in excavation permit; Conduct regular excavation inspection by competent person; All personnel to stand well back out of the line of fire when working near or around stored energy; Competent Operators to complete the works; SWMS/ JSA | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Excavation collapse; | Injury; Engulfment; Infrastructure damage; | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation | Engineering Battering where required; Benching where required; Shoring where required; Spotter to be in area when personnel are in excavations Use of Trench boxes for drainage excavations where required Temporary Works Design undertaken based on geotechnical information and the intended use of trench boxes; Trench boxes to be installed as per the engineered design requirements, as detailed in the Temporary Works Design; Should a change be required to the design or installed system, works shall cease and reassessment shall be undertaken in consultation with the Temporary Works Designer Administrative No placing of material, plant and loads near the edge of excavation; Spoils not placed closer than 1.5m to edge of trench;; Conduct regular excavation inspection by competent person i.e. Engineer or Site Supervisor; Trench box system shall be detailed on up-to-date drawings/plans; The persons who install and remove the ground support system shall be competent, and have awareness of the suppliers proprietary ground support system (Mabey product user guide); The shoring system shall be verified as correctly installed prior to use by a competent person, in accordance with the Temporary Works Design; When changes to the design or installed system are made, changes must be authorised and signed off by a competent person. Competent Operators to complete the works; SWMS/JSA | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39
| Slip and fall into excavation | Injury; | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation | Elimination Back fill excavations as soon as practical; Personnel to remain away from excavation edge at all time; Trench boxes, where used, to be fitted with hand rails and shall exceed ground level where possible Isolation Ensure where trench boxes do not exceed ground level, hand rails are installed Erect windrows / hard barricading around excavation – outside the excavation zone of influence 1V:1H (no less than 600mm where this is not possible) Engineering Safe means of ingress and egress - cut away steps, ladder, ramp Use of designated access platform and ladder system for trench box when applicable, alternatively use of access / egress ramp with trench box. Administrative Erect signage - EXCAVATION at entry point of excavation and along for approaching vehicles/ plant/personnel; Conduct regular excavation inspection by competent person i.e. Engineer or Site Supervisor; SWMS/JSA | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39
| Plant/Vehicle reversing into excavation | Injury; Infrastructure damage; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation | Isolation Erect bunting/windrows/hard barricades around excavation; Machinery restricted from working too close to trench (1.5 from edge); Machinery restricted from working inside the excavation zone of influence 1V:1H, (no less than 600mm where this is not possible); Administrative Ensure spotter in place where necessary; Conduct regular excavation inspection by competent person i.e. Engineer or Site Supervisor Competent Operators to complete the works; SWMS/JSA; | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39
| Person working in excavation crushed | Injury; | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation | Elimination Personnel not involved in excavation works to remain away from barricaded areas at all times When drainage equipment / trench boxes are being lifted into place, personnel shall stand clear of slew zone. No working under a suspended load at any time Engineering Benched and/or battered/ trench boxes used, if deeper than 1.5m; Safe means of ingress and egress-ladder, ramp, cut away steps Administration Competent Operators to complete the works; No one is to enter an open excavation > 1.5m deep unless excavation approved by a qualified person; Excavation inspected and approved by a competent person as safe to work in; Daily excavation Inspection completed by Engineer/ Site Supervisor; SWMS/JSA PPE Wear appropriate PPE | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39
| Person working in excavation being struck by falling object/plant | Injury; | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation | Engineering Double action movement to release bucket, avoiding accidental release Isolation Erect bunting/windrows/hard barricades around excavation; Personnel/spotter MUST not approach excavator unless bucket is on ground Administrative Loads must not be lifted, suspended or moved over a person under any circumstances; Spotter at ground level to monitor work activity and control work area in communication with operator; Competent Operators to complete the works; SWMS/JSA PPE Wear correct PPE | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39
| Unexpected encounter of contaminated material while excavating e.g. asbestos | Health risk; Environmental risk | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation WHS-SWP-5009 Asbestos | Engineering Erect Flagging/ barricading around unexpected contaminated material Administrative Manage material as per Safe Working Procedure; Competent Operators to complete the works; SWMS/JSA PPE Wear appropriate PPE P2 dust masks are to be available if required | Minor | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Stock pile control (dust and erosion) | Air pollution affecting vegetation, wildlife and health of people; Complaints; Legal non-compliance | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan WEM-SWP-104 Noise, Dust and Vibration Management | Administrative Adhere to Environmental Management Plan; Awareness training will be provided during the site induction; Area to be regularly sprayed with water via water truck to minimise air borne dust, Weekly environmental inspections and result of inspections recorded on WEM-FM-002 Weekly Environmental Inspection Checklist | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Fauna falling into excavation/ entrapment | Fauna distress, injury or death from becoming trapped and/or exposed; Legal non-compliance | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WEM-MP-001 Environmental Management Plan | Elimination Excavations to be backfilled as soon as possible; Engineering Permanent egress devices, such as ramps, should be installed to allow for the unimpeded movement of fauna into/out of the excavation; Administrative Adhere to Environmental Management Plan; Inspections of the excavation for fauna undertaken daily prior to work commencement | Minor | Unlikely |  | L2 |  | Site First Aiders Site Medic Emergency Channel 39
| Excavation during wet season/ saturated materials | Excavation collapse; Injury; Delays | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-081 Excavation | Administrative Conduct daily excavation inspection by competent person i.e. Engineer or Site Supervisor; Where risk has been identified post rain/ inclement weather no works in excavation to occur. Work area to be deemed safe by Site Supervisor prior to recommencement of work, Ticketed & VOCd Operators to complete the works; SWMS/JSA | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
Working near or around water | Person falling into water body | Drowning Hypothermia | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0023 Working Over or Near Water | Engineering Barricading to be established where necessary Bouyancy aid provided at waters edge Administrative Work area to be deemed safe by Site Supervisor prior to commencement of work, Spotter to monitor work activity at all times SWMS / JHA | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Tools, materials and or equipment falling into water body | Environmental risk Delays Equipment damage Environmental impact | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0023 Working Over or Near Water | Elimination Tools, materials and equipment to be securely stored away from waters edge as far as resonably practicable Engineering Barricading to be established where necessary Tools, materials and equipment to be securely stored away from waters edge as far as resonably practicable Waterlogged tooling / equipment to be tagged out and inspected for integrity before recommissioning Administrative Work area to be deemed safe by Site Supervisor prior to commencement of work, Spotter to monitor work activity at all times SWMS / JHA | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Hydrostatic Testing of pipework and associated componenets | Equipment failure / pipe, pipe joint failure | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Testing equipment to be tested before use Exclusion zone to be established before test commencement No personnel to be in test area while testing is underway Administrative Work area to be deemed safe by Site Supervisor prior to commencement of work, Spotter to monitor work activity at all times SWMS / JHA | Severe | Unlikely |  | Unlikely
| Unauthorised entry into test area | Personal injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Barricading / Signage Notice of test to be issued prior to test commencement Radio broadcast of test 30 minutes prior to test commencement | Moderate | Unlikely |  | Unlikely
Civil Works (Form Work, Concreting)
| Concrete splash over a wide area | Injury; Environmental impact | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction | Administrative Training in safe working procedure on concrete pumping; Provide supervision by competent person; Correct position and set up of boom pump. Prior to Boom Pump set up an assessment of Infrastructure and underground sevices required to ensure that they do not compromise the stability of the boom pump Clear communication to be maintained between truck driver, concreter or pump operator; During cleaning, remove all reducers and the rubber hose from the delivery line; Regular maintenance and inspection of equipment; Follow the concrete pumps manufacturer’s guidelines Always clean up concrete splashes as sson as possible Report all chemical spills to the relevant persons | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Burn on skin if contact with wet concrete | Injury; Irritation | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction | Isolation Only those directly involved in concreting should be in the work area Administrative Training in safe working procedure on concrete pumping; Provide supervision by competent person PPE Wear suitable PPE i.e. Safety boots, trousers, long sleeve | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Concrete splash to eye | Injury; Irritation | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction | Isolation Only those directly involved in concreting should be in the work area Administrative Training in safe working procedure on concrete pumping; Provide supervision by competent person; PPE Wear suitable PPE i.e. Safety glasses; Eye wash station (disposable bottles) located at site office | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Manual handling injuries | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction | Refer to Manual Handling - Section 14 Substitution Where required/feasible, use of laser screed for large area concrete pours Administrative Regular maintenance and inspection of equipment; Training in safe working procedure on concrete pumping; Manual handling awareness during site induction and toolbox; Provide supervision by competent person; Employ correct manual handling techniques at all times; Task stretching, warm up; Take 5; PPE Wear suitable PPE | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Hazardous Manual Tasks
| Ear damage & hand arm vibration syndrome | Injury Fauna distress | WEM-SWP-104 Noise Dust and Vibration Management | Elimination: Ensure vibratory tasks are not carried out excessivley or unneccesarily Ensure tasks are performed only within the designated working hours Inspect work areas for fauna before work commences Contact the responsible person if fauna is found to be entrapped and take appropriate removal actions Engineering: Use modern equipment with vibration-reducing features, such as vibration-resistant handles. PPE: Ensure required PPE is worn at all times. | Major | Rare |  | M11 |  | Site First Aiders Site Medic Emergency Channel 39
| Concrete cutting | Injury; Irritation Environmental impact | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-071 Manual Handling | Elimination: Ensure vibratory tasks are not carried out excessivley or unneccesarily Ensure tasks are performed only within the designated working hours Engineering: Use modern equipment with vibration-reducing features, such as vibration-resistant handles. PPE: Ensure required PPE is worn at all times. | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
| Grinding concrete fill around conduit entrance to culvert | Injury; Irritation to respiratory tract Environmental impact | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-071 Manual Handling WEM-SWP-104 Noise Dust and Vibration Management | Substitution Use mechanical aids and additional manpower for heavy grinding tasks Administrative Employ correct manual handling techniques at all times; Isolation Ensure concrete dust is managed to be ALARP to minimise personal and environmental impact Clear and accessible work area allowing for safe movement of people, equipment and materials; Raise awareness at site induction and toolbox meeting; Take 5 PPE Wear appropriate P2 classification respirator, gloves and double eye protection along with normal site PPE when performing grinding task | Moderate | Possible |  | Possible |  | Site First Aiders Site Medic Emergency Channel 39
| Plant accident | Injury; Death; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Isolation Only those directly involved in concreting should be in the work area; Segregated work area, actively managed and barricaded around pump truck; Administrative Regular maintenance and inspection of plant & equipment; Ensure concrete pump operator is competent; Clear communication to be maintained between truck driver, concreter or pump operator; Ensure work area is accessible for concrete truck; Follow the concrete pumps manufacturer’s guidelines; PPE Wear appropriate PPE | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
| Early Morning Pours Poor Visibility, Fatigue | Injury; Damage to plant | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Engineering Sufficient lighting to be supplied at pour area; Temporary lighting to be setup by dayshift prior to works Administrative Day shift to ensure all areas and access are clear before changeover early morning crew come to site; Ensure good housekeeping dispose waste and stow equipment safely, Sufficient Traffic Management to be in place prior to pour commencement (inclusive of reflective posts and lighting), Fuelling up on night shift is not permitted fuelling up will be done by the day shift, Fatigue management to be on going and monitored by Site Supervisor/ HSE Advisor; Personnel to complete WHS-FM-023 Fatigue Assessment where required; Personnel working on early morning shifts are to finish early the day prior and early the day post morning pour shift off before returning to work. This is to be monitored by HSE Advisor and site supervisor PPE All personnel involved in early morning works to wear hi-vis reflective strip clothing/ shirt/ Vest and clear safety glasses | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Working with reinforcement | Manual task injury; Scratches or cuts to body | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WHS-SWP-304 Concrete Slab Construction | Isolation Place protective caps over exposed ends of vertical and starter bars; Administrative Obtain assistance to handle heavy or awkward lengths and sheets; Adopt ergonomically sound position; PPE Wear long sleeved shirts and pants; Wear approved type gloves | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Walking on rebar | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WHS-SWP-304 Concrete Slab Construction | Isolation Place protective caps over exposed ends of vertical and starter bars; Engineering Installation of Safety mesh above 220x220 SQ Administrative Walk on the top bars of the prepared mat PPE Wear Safety footwear | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
| Placing Reinforcement | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-071 Manual Handling | Refer to Manual Handling - Section 14 Substitution Use mechanical aids and additional manpower for heavy loads; Administrative Manual handling induction site induction; Take 5; Employ correct manual handling techniques at all times; Clear and accessible work area allowing for safe movement of people, equipment and materials; Raise awareness at site induction and toolbox meeting PPE Wear appropriate PPE e.g. Safety boots, gloves, Safety glasses etc. | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
| Bending reinforcement | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-071 Manual Handling | Elimination Ensure machine is indoors, is completely dry and is not operated in wet or damp conditions Substitution Use mechanical aids and additional manpower for heavy loads Isolation All bending work should be conducted indoors Engineering Mount and secure machine on level surface capable of carrying the weight of the machine Administration Inspect the machine before each use Training in how to safely operate the machine Ensuring to not attempt to bend rebar outside of the manufacturer's specification PPE Eye protection glasses Wear approved gloves Class 2 hearing protection | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Cutting Reinforcement | Injury Environmental impact caused by discarded metal offcuts and cutting discs | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-071 Manual Handling | Substitution Use battery operated/cordless grinder; Cutting disc thinner then 1.5mm must not be used; Isolation Shielding of grinding operations; All cutting work must not be conducted near any ignition sources; Isolation Ensure all offcuts and discarded consumables are collected and disposed of correctly Administration Hot work permit; Tool handle must be attached; Use of fire spotter if required with the provision of firefighting equipment i.e. 9KG extinguisher; Assess wind conditions; Check equipment before use PPE Double eye protection (glasses and face shield); Wear approved gloves | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Batch Plant Setup and Operation
| Position water and admixture Tanks Placement and positioning of Batch hut and associated Offices and crib buildings | Manual handling: moving/ install of tanks/ drums Availability of Mechanical Lifting equipment Untrained / unskilled personnel Poor install/set up resulting in trip hazards and/or dropped objects Damage to natural flora/fauna habitats Environmental impact caused by unintended hydrocarbon/chemical release | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Isolation Access and egress to batch plant to be maintained at all times; Works are to be appropriately delineated/barricaded; Locate tanks/pallets and hose away from frequently used areas or if possible bury hoses underground No personnel to work/ be under suspended loads Engineering Ground to be appropriately compacted for required operations; Obtain assistance or the use of mobile plant to move tanks into position; Allow enough room for access by mobile plant to fill tanks or replace drums Administrative Correct manual handling and lifting techniques; Spotter to be utilised as required; Only ticketed/ VOC'd operator to be used; Operator to inspect ground prior to mobilising equipment to a new task area; Correct tool to be used for manual handling / hammering tasks; Signage in place outlining single entry point to area of excavation which is controlled by the operator or spotter; Inspection of areas for loose rock, fauna or similar prior to entry; All task documentation to detail equipment roll-over specific emergency response plan; Task specific JSA to be utilised for vehicle/plant recovery PPE Wear appropriate PPE at all times; Wear gloves when handling pipe/hose | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Connection of Batch Plant | Electrocution/ Stored energy | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Isolation Ensure compressor has been drained of stored energy before connection; Ensure all taps turned off before connection of water tank / chiller / batch pump; Cam lock fittings on all connection points; Ensure all guarding in place and un-damaged in transit Engineering Ensure earth stakes inserted and connected. All electrical connection points are plug in Administration Check all leads, plugs and switch’s for damage in transit before connecting; Licensed Electrician for connection to Generator; Licensed Electrician to conduct earth leakage test’s, submit documentation for authorisation; Pre-start check on Gen set before starting; Check for correct operation of electrical items singularly; Ensure appropriate SCEE Isolation permits/training in place prior to set up | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Exposure to hazardous Materials & Thermal Heat | Admixture: from previous job in hoses. Environmental (spills) | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Engineering Allow water to run before filling tanks. (Beware of Hot water from taps and hoses if not used for a period of time); Administrative Do not drink the water from hoses and tanks at the plant unless tested and deemed to be safe e.g. potable water; Ensure residue admixture removed from line - Flush admixture hoses with water before demobilisation of plant Ensure spill kits are available, and that personnel are trained in their use and the correct waste disposal procedures. PPE Gloves are to be worn whilst handling hoses | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
|  | Personnel, other workers or flora/fauna nearby in the workspace exposed to hazardous chemicals such as volatile vapours, fumes, airborne hazard particulates Personnel exposed to hot motors, exposed flames, flashback, hot fluids likely to cause burns or scalds. High ambient temperature work environments | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Engineering All portable machinery and equipment shall be regularly maintained to help reduce high noise, vibration, temperature and dust levels Administrative SDS’s are to be available for all admixtures brought and used onsite. SDS to be stored in site office for batch plant specific chemicals Chemical storage and use in accordance with SDS First aid kit (and suitability) trained personnel to be at immediate work area All chemicals to be bunded or stored appropriately Adequate stocked and maintained spill kits to be at immediate work area Work areas to be have adequate ventilation Heat and Hydration to be monitored/ discussed at pre-start and toolboxes JSA/SWMS/ Take 5, Emergency Response Plan involving spills PPE Appropriate PPE utilised e.g. appropriate gloves, P2 dust mask | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Washout of agitator truck and control of waste concrete | Environmental damage cause by incorrect control of waste concrete | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan | Isolation Work area assigned by SCEE and Westforce Construction; Concrete pump truck to be washed out at designated are at pour site; Bunded area plastic lined set up for washout near to the pour site; Site drainage to be set up in accordance with site environmental licence; All sediment laden runoff to be captured runoff. Conduct regular environmental inspections of the drainage areas. Administrative Excess concrete to be used as blinding and/or removed by Hanson to Gelorup quarry, to be recycled and reused for road base material. Environmental Management Plan | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
Civil Works (Form Work & Concreting)
Formwork Erection (traditional formwork) | Sustain injury whilst installing/cutting formwork | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction; WHS-SWP-305 Formwork; | Elimination Ensure that wooden formwork is free of nails etc. before handling; Ensure that timber is free of concrete, dirt etc. before cutting Isolation Ensure clear and accessible work area allowing for safe movement of people, equipment and materials Substitution Use mechanical aids and additional manpower for heavy loads Engineering Use correct tools Install personnel access/egress steps or ramps Administrative Raise awareness at site induction and toolbox meeting; Obtain assistance to handle heavy or awkward lengths and sheets; Adopt ergonomically sound position; Take 5; Refer to 'Manual handling' - Section 14 PPE Wear appropriate PPE e.g. Safety boots, gloves, Safety glasses etc. | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Hazardous Manual Tasks
| Formwork collapse before and after loading | Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction; WHS-SWP-305 Formwork; | Isolation Establish exclusion zone where formwork is to be erected Administrative Construction and erection to be carried out by competent personnel; Erection to be systematically carried out in accordance with manufacturer's or designer's instructions; Supervision by Site Supervisor; Formwork to be regularly inspected by Project Engineer; Inspection to be carried out before formwork is loaded, after loading, after repairs, alteration or additions to formwork; Avoid 'point' loading on any part of the formwork by placing concrete evenly | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
Formwork Dismantling (traditional formwork) | Formwork collapse | Injury; Death | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction; WHS-SWP-305 Formwork; | Administrative Inspection by Project Engineer before dismantling; Dismantling to be carried out by competent persons | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Sustain injury while dismantling formwork | Manual task injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction; WHS-SWP-305 Formwork; | Isolation Establish exclusion zone where formwork is to be dismantled Engineering Use correct tools Administrative Obtain assistance to handle heavy or awkward lengths and sheets; Adopt ergonomically sound position; PPE Wear appropriate PPE i.e. hard hat, Safety boots, Safety glasses, gloves | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Hazardous Manual Tasks
| Formwork collapse | Injury; Death | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction; WHS-SWP-305 Formwork; | Isolation Establish exclusion zone where formwork is to be erected or dismantled; Formwork props must not be removed prior to hook up of formwork where required Engineering Where mechanical aid (crane) needed to remove formwork pans, adhere to controls listed in Section 11: Cranage & Rigging Administrative Formwork to be designed & certified by Formwork Designer; Formwork to be inspected by Project Engineer before the formwork is loaded, after loading and after repairs to formwork are made; Erection and stripping to be carried out by competent personnel; Erection and dismantling to be systematically carried out in accordance with manufacturer's or designer's instructions | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39
| Slip, trip or fall from height | Injury; Death | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction; WHS-SWP-305 Formwork; | Isolation Remove any objects that may obstruct personnel Engineering Install edge protection where required; Administration Formwork to be inspected by Project Engineer before the formwork is loaded, after loading and after repairs to formwork are made; Continuous supervision by Project Engineer and Site Supervisor; Adopt ergonomically sound position; PPE Wear appropriate PPE i.e. safety boots and hard hat | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Falls
| Sustain injury while installing/dismantling formwork | Manual task injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan C2761-WHS-MP-001 WHS Management Plan WOP-SWP-031 Concrete Construction; WHS-SWP-305 Formwork; | Refer to Manual Handling - Section 14 Isolation Establish exclusion zone where formwork is to be installed/dismantled Engineering Use correct tools; Mechanical aid used where required; Adopt ergonomically sound position Administrative Obtain assistance to handle heavy or awkward lengths and sheets; PPE Wear appropriate PPE | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Hazardous Manual Tasks

## KBESS GIS Commissioning (hidden)
Register Type | Project Risk Register
Project(s) | KBESS
Approved by | Project Manager - Steven Roger
Task / Activity | Hazard | Risk (un-wanted event) | Genus Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
NHOA Battery Commissioning
Mobilisation of personnel | Unqualified personnel | Inadequate competency of personnel. Breach of licensing regulations | Genus Recruitment Onboarding and Induction Procedure | > Reference and competency checks procedure followed > Training needs analysis / matrix > Training Matrix to include role specific requirements > Project induction | Moderate | Rare | 2 | L5 | Accept | Ensure new employees are integrated with existing long term employees. | Supervisor | Ongoing
Mobilisation of subcontractors | Contractor engagement | Unfamiliarity with Genus and client procedures. Conducting work unsafely or in conflict with Genus or client procedures. High risk and/or specialised tasks. Introduced hazards to the workplace. | Genus Recruitment Onboarding and Induction Procedure Contractor Code Compliance & SHE Assessments | > Contractor and Supplier Management Procedure > Contractor pre-qualification process and Register > Contractor induction process > KPIs for contractor monitoring / assurance activities | Moderate | Unlikely | 2 | M7 | Accept
Mobilisation to site for personnel | Site access not approved | Delay in mobilisation of personnel | Genus Recruitment Onboarding and Induction Procedure | > BSO to ensure personnel meet site access requirements | Moderate | Rare | 2 | L5 | Accept
Fitness for work | Personnel impaired by drug & alcohol | Injury / illness as a result of impaired fitness for work | Genus Fitness for Work Policy & Procedure & Drug and Alcohol Procedure | > Daily BAC Testing at Pre-Start or entering site. > D&A testing program (pre-employment, random, for-cause, blanket) > Project to be included on random sample schedule > Conditions of employment > Employee Assistance Program (EAP) | Moderate | Unlikely | 2 | M7 | Accept
Weather Conditions | Adverse / Inclement Weather - Strong Winds / Lightning Flooding | Loose or flying materials. Lightning Strikes. Floods. Personal Injury Property Damage Environmental Impact | KBESS SHEMP Genus Environmental Procedure Working Near Live Traffic and Mobile Plant | > Monitoring BOM > Conducting pre -forecasted storm weather reports > Tie - down for equipment and materials. > Storm water run off in to designated detention basins. > Communicate weather conditions to supervisors as per weather front details. > 30 / 30 rule lighting detected on track within 10 kms of project area. > Secure all plant and machinery on firm stable higher ground. | Major | Unlikely | 3 | M12 | Accept
SIMOPS Working near commissioning activities being conducted by the owner or client on the CAT-L Battery Cabinets or associated equipment | Energised battery cabinets or NHOA equipment upstream / downstream outside of GIS control Cold or Hot Commissioning | Electric Shock, Arc Flash Burns, Fire Explosion, Thermal Runaway Electrocution. MTI RWI LTI Fatality | GIS KBESS SHEMP GIS Commissioning Management Plan Authority to Work Procedure Isolation & Tagging Procedure High Voltage Switching & Isolation Procedure, NOE Procedure Synergy / NHOA KBESS Construction Management Plan NHOA Commissioning Management Plan | > Owners and clients to provide GIS with commissioning management plans and procedures to identify the process for commissioning CAT-L Battery Cabinets and other associated equipment in the KBESS project outside GIS control. > All GIS personnel that will be working within or on the boundary to the clients commissioning processes to be trained and verified competent to work near or on these works. > Urgent decisions regarding any SIMOPS shall fall under the responsibility of the GIS Construction Manager and the GIS Commissioning Manager, who through joint agreement, shall reach conclusion as to which activity takes precedent. > All areas which fall under the responsibility of the Commissioning Manager shall be deemed as Restricted Areas. Restricted areas shall be appropriately demarcated and shall have warning signs erected. All work in restricted areas must be performed with a valid authority to work and entry is also restricted to authorised/permitted personnel. > All pre-commissioning and commissioning activities will be carried out under a commissioning permit to work system. > Prior to the energisation of plant and apparatus, a Notice of Energisation will be issued. All systems, sub-systems, plant and apparatus which are undergoing commissioning must be clearly and easily identifiable, including barricades and signage advising of the energisation and ongoing commissioning activities. > GIS to place controls such as locks / barriers at their point of boundary to prevent energisation to works being conducted by GIS. > All pre-commissioning and commissioning activities will require as a minimum a Safe Work Method Statement (SWMS) | Major | Unlikely |  | M12 | TBC | All parties will use the same commissioning process systems including; Commissioning, Training Inductions, refreshers, Authorised recognition - Stickers, Inductions commissioning. Authorisation to undertake isolations as per eth entity i.e. NHOA / GIS Permitting process. Visually identified with clear notifications and documentation. Process, SWMS, JHAs, Take Controls. Equipment locks, barriers signage etc. Consultation, Pre-starts, NOE's, Toolbox Daily, Site meetings between NHOA & GIS etc. | M Wilson | Completed
GIS Commissioning Works
Personnel conduction pre-commissioning and commissioning activities. | Personnel not competent to undertake commissioning activities | Exposure to energised installations or equipment. Damage to equipment. | GIS KBESS SHEMP GIS Commissioning Management Plan KBESS Commissioning Training NHOA Commissioning Management Plan | > All KBESS Commissioning Personnel to complete Synergy/NHOA/GIS commissioning training. > Register for personnel authority to work holder > Daily SIMOPS meetings NHOA & GIS > Workers able to comply with Authority to Work Procedure > Isolation and Tagging procedure > High Voltage Switching & Isolation Procedure > NOE Procedure | Major | Unlikely | 4 | M12 | TBC | Daily SIMOPS meetings NHOA & GIS | K Greig / M Wilson NHOA Commissioning Management
Electrical Workers | Licenced Electrician works - Initial works connecting site facilities | Unqualified electrical contractor / electricians. Performing electrical work without license | SHEMP Onboarding Procedure Energy and Isolation Procedure | > No Live Electrical Works Apart from testing and under isolation / permit conditions. > SWMS, JHA and Take 5 are implemented and acknowledged prior to works commencing. > Live testing works - Electricians and Electrical support workers in area to be CPR LVR qualified. > Electrical workers are licensed and qualified to undertake scope of work. > All electricians to be licensed and experienced for scope of work. > Training Records will be maintained by site BSO in Training Matrix | Major | Unlikely |  | M12 | TBC
Electrical Workers conducting commissioning works | Inadequate risk assessment for working on commissioning systems | Exposure to energised installations or equipment. Faulty or not correctly built equipment. Exposure to electric shock or electrocution Damage to equipment. | GIS KBESS SHEMP Risk and Opportunity Procedure GIS Commissioning Management Plan Authority to Work Procedure KBESS Commissioning Training | > No Live Electrical Works Apart from testing and under isolation / permit conditions. > SWMS, JHA and Take 5 are implemented and acknowledged prior to works commencing. > Live testing works - Electricians and Electrical support workers in area to be CPR LVR qualified. > Electrical workers are licensed and qualified to undertake scope of work. > All electricians to be licensed and experienced for scope of work. > Training Records will be maintained by site BSO in Training Matrix > Commissioning Toolbox Awareness session - Provide information and instructions on pre-commissioning works - Either party may be able to delivery training and issue awareness TBT stickers. | Moderate | Unlikely |  | M7 | TBC | > Commissioning Toolbox Awareness session - Provide information and instructions on pre-commissioning works - Either party may be able to delivery training and issue awareness TBT stickers. | K Greig / M Wilson NHOA Commissioning Management | Completed
Commissioning Tools and Test Equipment | Tools and equipment inadequate for commissioning or calibration requirements | Exposure to energised installations or equipment. Faulty or not correctly built equipment. Exposure to electric shock or electrocution Damage to equipment. | GIS KBESS SHEMP Risk and Opportunity Procedure Measuring and Monitoring Procedure GIS Commissioning Management Plan Authority to Work Procedure KBESS Commissioning Training | > A register will be maintained of all commissioning tools and test equipment and their issuance for use controlled. > All test equipment must have a valid NATA accredited calibration certificate (i.e. within the last 12 months) and this level of calibration maintained throughout the currency of the project. > All test equipment calibration certificates will be maintained in a calibration register (within the CMD) > Any test equipment used in the process of carrying out pre-commissioning and commissioning testing must be recorded on the supporting documentation as follows: • Test Equipment Description • Model • Serial Number • Date of Calibration | Moderate | Unlikely |  | M7 | TBC
Use of Power Tools During Commissioning Activities | Use of electrical Power Tools for Electrical Commissioning Works | Dropped Objects Electric Shocks | SHEMP Working at Heights Prohibited and Restricted Items Procedure / List Hazardous Manual Handling Procedure | > Follow Working at Height Procedure > Tool lanyards > Electrical equipment to have current electrical inspection tag. (Quarterly)> Electrical leads and equipment to be inspected prior to use. > Lead lengths - 30m maximum length for any leads, all leads off the ground / off-steel work. Ensure cables are protected from damage. > Electrical leads to be raised off the ground with lead stands at 2.4m. > Electrical equipment to be inspected before use > RCD's to be used > Generator to be earthed as required | Major | Unlikely |  | M12 | TBC
Work in de-energised systems | Systems not de-energised Not isolated from energy sources | Electrical shock Arcing, explosion or fire | SHEMP Onboarding Procedure Energy and Isolation Procedure | > No live work to be conducted on LV or HV > Isolation Procedures must be followed. > All electrical service to be tested and positively identified as de-energised prior to touch. > Clear Air Breaks on electrical cables where terminations are being conducted. > Test for dead adjacent electrical components when working within their vicinity. > Use intrinsically safe insulated protected tools. | Major | Unlikely |  | M12 | TBC
Working near energised electrical equipment or components | Energised apparatus | Electrical shock Arcing, explosion or fire | SHEMP Onboarding Procedure GPG Electrical Safety Standard Energy and Isolation Procedure | > No live work to be conducted on LV or HV > SWMS Working near Live Electrical Equipment or Components > Work is only permitted for GPG employees and its subcontractors when: > The equipment has been de-energized and isolated; or > Separated by barriers or an appropriate distance based on a risk assessment. > Approval from GPG Company EGM with consultation with client / network owner. > Seek approved Access or and Isolation Permits from Client / Net Work Provider. > Isolations on plant or equipment to be performed only by approved competent qualified experienced isolation officers who understand the system being isolated. > Ensure you are working on the latest revision drawings. > All personnel working on cable trays / cables or equipment that have the potential of becoming live or are live must place a personal danger tag and lock on as per the isolation procedure follow above process and test for dead procedure. > Always test for dead with appropriate calibrated testing equipment. (Refer to Selection of Test Equipment in rear of this SWMS). > Barriers shall be of suitable material to effectively separate electrical workers from adjacent energised electrical equipment. > Conductive items such as tape measures, rules, reinforced tapes, ladders, elevating work platforms, scaffolding, and guards on portable lamps, not being used on or near exposed energised conductors or live conductive parts. > Insulated tools and equipment shall be of an approved type and shall be in good order, regularly maintained and tested where required. > Insulated Tools shall be visually inspected before each use for any sign/s of damage or deterioration of the insulation. > All electrical service to be tested and positively identified as de-energised prior to touch. > Clear Air Breaks on electrical cables where terminations are being conducted. > Defective items shall be tagged accordingly and removed from service. > Insulating Mats and Insulating Covers shall be suitable for the voltage at which used. > PPE – Protective clothing worn by electrical workers Insulted Gloves – (please refer to the Table in these SWMS for types of Insulated Gloves). Safety Observer – When working within the Minimum Approach Distance to Live electrical Components a competent qualified Safety Observer will be required. | Major | Unlikely |  | M12 | TBC
Pre-Commissioning Checks | Systems not adequate or faulty or not constructed to a safe level prior to energisation. | Exposure to energised installations or equipment. Faulty or not correctly built equipment. Exposure to electric shock or electrocution Damage to equipment. | GIS KBESS SHEMP GIS Commissioning Management Plan KBESS Commissioning Training | > ITR’s, marked up copies of P&ID’s, SLD’s. Logic Diagrams, System Functional Descriptions etc. will be provided as evidence of the completion of this work. > OEM Manuals etc. to identify process and system is operational. > Verify instrumentation loop checks, control functional checks, and the initial energisation of control supplies and plant system peripherals prior to the equipment being energised. | Major | Unlikely |  | M12 | TBC
Outstanding Defects and Omissions, Informal Walk Downs | Systems not adequate or faulty or not constructed to a safe level prior to energisation. | Exposure to energised installations or equipment. Faulty or not correctly built equipment. Exposure to electric shock or electrocution Damage to equipment. | GIS KBESS SHEMP GIS Commissioning Management Plan KBESS Commissioning Training | > Ten days prior to the targeted Handover from Construction to Commissioning date an informal system walkdown will be carried out between all stakeholders (i.e. subcontractor, Construction & Commissioning) and a ‘works to go list’ developed. > Outstanding defects and omissions (i.e. punch lists) are identified, categorised and agreed as part of the Handover from Construction to Commissioning process including those carried over from the ‘works to go’ list. > Each punch item is entered into the Completions Management Database (CMD) punch list module for subsequent assignment of responsibility and closure tracking. | Major | Unlikely |  | M12 | TBC
Construction Verification and Handover from Construction to Commissioning | Inadequate handover or construction activities incomplete | Exposure to energised installations or equipment. Damage to equipment. Project delays | GIS KBESS SHEMP GIS Commissioning Management Plan GIS Handover from Construction to Commissioning Procedure KBESS Commissioning Training | > Formal handover from Construction to Commissioning and is marked by the use of a Handover Certificate Construction to Commissioning. > Works to be handed over are inspected and any outstanding defects and omissions are agreed and recorded, all associated construction verification documentation and as built drawings are reviewed for completeness. > All delegates on the handover certificate to be endorsed prior to commencement of commissioning works. > Construction Boundary locks to be removed and relocated to next stage of the commissioning phase. | Major | Unlikely |  | M12 | TBC
Switchyard Switchroom Access once construction commissioing and handover to client. | Unauthorised access to Switchrooms and Switrchyards. | Exposure to energised installations or equipment. Damage to equipment. Project delays | GIS KBESS SHEMP GIS Commissioning Management Plan GIS Handover from Construction to Commissioning Procedure KBESS Commissioning Training | > All authorised personnel to complete the Switchyard Switchroom Access Inductions. > Switchyard / Switchroom access gates to be closed and locked to unauthorised personnel during the Going Live phase of commissioing handover process. > Commissioning Manager to maintain the Authority to Work register for access to approved authorised competent personnel to Switchyard's and Switchroom. > The Manager or Superintendent to implement and maintain access keys for gates to Switchrooms and switchyards. | Major | Unlikely |  | M12
Notice of Energisation | Incorrect or no process for communicating that energised equipment will commence | Exposure to energised installations or equipment. Damage to equipment. | GIS KBESS SHEMP GIS Commissioning Management Plan Authority to Work Procedure Isolation & Tagging Procedure High Voltage Switching & Isolation Procedure, NOE Procedure KBESS Commissioning Training | > Handover Certificate has been issued to commissioning team that the control of plant and apparatus has been transferred from construction. > Boundary Isolations is reviewed and identified in order to isolated any downstream systems not under commissioning control. > A Notice of Energisation is prepared detailing the plant and apparatus to be energised, any boundary isolations to be implemented and/or released and all new boundary isolation keys secured in a boundary isolation lockbox jointly under the control of the Permit Office, Construction Manager and Commissioning Manager. > NHOA will attach their boundary locks onto the same boundary control lock box for isolations. that are defined as the same boundarys. > The Notice of Energisation is signed and communicated to the workforce via pre-starts, notice board etc as per local management instruction. > A minimum of 48 hours must have elapsed between then issuance of a NOE and subsequent energisation. > The NOE paperwork is now completed, and any boundary points released. > The system or part thereof and all plant/apparatus detailed within the NOE are now considered energised and from this point it is mandatory to have access to that plant or equipment using the Project Isolation and Lockout Procedures. | Major | Unlikely |  | M12 | Accept
Commissioning Checks | Systems not adequate or faulty or not constructed to a safe level prior to energisation. | Exposure to energised installations or equipment. Faulty or not correctly built equipment. Exposure to electric shock or electrocution Damage to equipment. | GIS KBESS SHEMP GIS Commissioning Management Plan KBESS Commissioning Training | > Checks include the use of energy sources, followed by the initial operation of sub-systems and systems for their intended purpose. > Checks verify that the results in the plant and/or apparatus achieving the status of safe for automatic operation. > ITP’s, ITR’s and the Commissioning Test Procedures will be provided as evidence of the completion of this work. > AS built drawings to be reviewed | Major | Unlikely |  | M12 | TBC
Start Up and Operational Testing | Systems not adequate or faulty or not constructed to a safe level prior to energisation. | Exposure to energised installations or equipment. Faulty or not correctly built equipment. Exposure to electric shock or electrocution Damage to equipment. | GIS KBESS SHEMP GIS Commissioning Management Plan KBESS Commissioning Training | > Operational testing involves the start-up and testing of the plant as a single entity throughout its load range in order to confirm that the facility operates as per the design and contract specification. > ITP’s, ITR’s, Commissioning Test Procedures and Test Reports will be provided as evidence of the completion of this work. > AS built drawings to be reviewed. > Authorised by GIS for managing access to the HV apparatus / switchyard when energised, > Locked gates maintained by isolation officer. > Designated walkways updated TMPs > Communication on access controls to workers in HV/ apparatus switchyard | Major | Unlikely |  | M12 | TBC
Grid Code Compliance Tests, Functional Test, Performance Tests & Reliability Tests | Systems not adequate or faulty or not constructed to a safe level prior to energisation. | Exposure to energised installations or equipment. Faulty or not correctly built equipment. Exposure to electric shock or electrocution Damage to equipment. | GIS KBESS SHEMP GIS Commissioning Management Plan KBESS Commissioning Training | > Tests shall demonstrate the facility’s compliance all testing requirements. | Major | Unlikely |  | M12 | TBC
Working on or near Energised Equipment that has been commissioned
Energy Isolation | Live Electrical Components | Electric Shock Fire & Explosion | SHEMP Electrical Policy Electrical Standard Energy and Isolation Procedure | > No live work to be conducted on LV or HV > Isolation Procedures must be followed. > All electrical service to be tested and positively identified as de-energised prior to touch. > Clear Air Breaks on electrical cables where terminations are being conducted. > Test for dead adjacent electrical components when working within their vicinity. > Use intrinsically safe insulated protected tools. | Major | Unlikely |  | M12 | TBC
Restoring power | Live Electrical Components | Electric Shock Fire & Explosion | SHEMP Electrical Policy Electrical Standard Energy and Isolation Procedure | > No live work to be conducted on LV or HV > Isolation Procedures must be followed. > All electrical service to be tested and positively identified as de-energised prior to touch. > Clear Air Breaks on electrical cables where terminations are being conducted. > Test for dead adjacent electrical components when working within their vicinity. > Use intrinsically safe insulated protected tools. > Isolation authority to verify with construction / commissioning manager that systems are complete tests NOEs issued and are acceptable and handover back to commissioning prior to locks being removed. > Handover certificates completed. > NOEs to be issued in Pre-starts. > Permits to be closed. > Isolation locks removed. > Plant and equipment re-energised. > Verification tests conducted to ensure system is operational. | Major | Unlikely |  | M12 | TBC
EMERGENCY
Emergency Incident | Fire, explosion, medical emergency, utility strike, Hazchem spill / release, severe weather, bomb threat, intruder Thermal Runaway | Personal injury or fatality | KBESS SHEMP KBESS Emergency Fire Response Plan | > GIS KBESS Emergency Response and Fire Management Plan. > Contacted emergency services if potential to catch fire - DFES > Chief Warden to notify the Emergency Services of Emergency and pick up points. > Gate 7.2 is main pick up point for access to BESS area. > Trained First Aiders / First Responders > Scheduled servicing and inspection of emergency and fire fighting equipment > Stocked First aid kits in First aid room. > Natural ventilation for fuel and Hazchem storage areas > Spill Kits Booms / socks, Tarpaulins for containment of potential > Emergency WA RSS feed monitored by SHEQ department > Drills / testing frequency as per Emergency Drill Schedule. Formal effectiveness review following each evacuation (drill or actual) > Genus Plus Group SMS service for communications | Severe | Unlikely | 4 | H17 | TBC

## Electrical
Register Type | Project Risk Register
Project(s) | CBESS BOP
Approved by
Task / Activity | Hazard | Risk (un-wanted event) | Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
Cable Installation
Installation of cable tray in culverts | Fall from height Fauna interaction / trapped fauna | fall into culvert resulting in injury Fauna distress Injury to personel caused by trapped fauna | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0017 Working at Height (High Risk) SYN-PRC-HSA-0010 Safe Work at Height Procedure | Barricade / exclusion of personnel from proximity to culvert edge Signage Culverts inspected for fauna before entry Ensure culverts have adequate fauna escape routes Use of dedicated crossing points with engineered solution to cross culverts Dedicated process for entry to, and egress from, culverts JHA, Take 5 Good housekeeping practices, removal of equipment and materials not required out of the culvert area Star Inspections | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Falls
| Sharp edges | cuts/lacerations | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | PPE- correct gloves used to mitigate task hazard JHA, Take 5 Star Inspections | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Restricted work area | pinch points/restricted space resulting in hand or finger injuries/abrasions Debris left in bottom of culvert Dust and / or debris blown from culvert into eyes | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Awareness of line of fire situations PPE- correct gloves used to mitigate task hazard Foam backed goggles to be worn when work in culverts is to be carried out Good housekeeping practices, reqular cleaning of culverts to remove debris Good housekeeping practices, removal of equipment and materials not required out of the culvert area JHA, Take 5 Star Inspections | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39
| Uneven ground/walking over existing cable tray | musculoskeletal injury, rolled ankle, slip/trip | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0006 Manual Handling SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Minimise culvert access where possible, essential personnel only Work planning - sequencing and staging of work to reduce scope of impact JHA, Take 5 Use of dedicated crossing points with engineered solution to cross culverts Good housekeeping practices, removal of equipment and materials not required out of the culvert area Star Inspections PPE - well fitted boots, laced correctly to provide ankle support | Major | Likely |  | H15 |  | Site First Aiders Site Medic Emergency Channel 39
Installation of conduits around culverts | Hand tool / PVC pipe cement usage while assembling conduit Open conduit ends | Cuts / Abrasions Skin irritation Environmental concerns Muscle strain from repetetive bending / unbending Environmental impact from spilt pipe cement Fauna becoming entrapped in open conduit runs | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0006 Manual Handling SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Correct PPE to be worn when cutting conduit - Cut 5 gloves Correct gloves as per SDS when using PVC pipe cement Ensure absorbent mat is under conduit to collect spills / drips when joining conduit with PVC pipe cement Ensure empty PVC pipe cement containers are disposed of correctly Pre task stretches and regular breaks while assembling conduit Conduit ends to be covered to prevent fauna entrapment | Moderate | Unlikely |  | M6 |  | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Hazardous Manual Tasks
| Fall from height | Fall into culvert resulting in injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0017 Working at Height (High Risk) SYN-PRC-HSA-0010 Safe Work at Height Procedure | Barricade / exclusion of personnel from proximity to culvert edge Signage Use of dedicated crossing points with engineered solution to cross culverts Dedicated process for entry to, and egress from, culverts JHA, Take 5 Good housekeeping practices, removal of equipment and materials not required out of the culvert area Star Inspections | Moderate | Unlikely |  | Unlikely |  | WA Code of Practice Managing Risk of Falls
| Heavy lifts on uneven slippery ground | Musculoskeletal injury - strain Slips / Trips / Rolled Ankles Cuts / abrasions to hands Sharp Edges | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0006 Manual Handling SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | 2 person / mechanical lifts if required Be aware of surroundings Pre Task lift assessment Pre task stretches / warm up JHA / Take 5 Clear work area before task commencement, good housekeeping practices Correct PPE to be used - Cut 5 gloves when lifting | [5 empty] | WA Code of Practice Hazardous Manual Tasks
| Hand tool usage whilst securing conduits in place | Musculoskeletal injury - strain / strains from installing star pickets and lifting Slips / Trips / Rolled Ankles Cuts / abrasions to hands from hand tool usage Sharp edges on conduit and wooden supports Noise from impact driver | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0006 Manual Handling SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Awareness of line of fire situations - Know where your hands are Use star picket driver to install star pickets - Wear impact rated gloves Correct PPE (Cut 5) when handling objects with sharp edges JHA, Take 5 Star Inspections Ear plugs to be worn in noisy environments Good housekeeping practices, removal of equipment and materials not required out of the work area | [5 empty] | WA Code of Practice Hazardous Manual Tasks
Installation of electrical equipment | Heavy equipment | musculoskeletal injury - strain | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0006 Manual Handling SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Use lifting aids/mechanical lifting equipment Team lifts Pre-task lift assessment Task stretching, warm up JHA, Take 5 Good housekeeping practices, removal of equipment and materials not required out of the work area prior to installing equipment Star Inspections | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Hazardous Manual Tasks
Installation of cable in tray | Sharp edges | cuts/lacerations Wind borne dust and debris blown from culvert into eyes | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | PPE- correct gloves used to mitigate task hazard cable ties to be cut such that sharp edges are not present Foam backed goggles to be worn when work in culverts is to be carried out JHA, Take 5 Star Inspections | Moderate | Unlikely |  | M7 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Cable pulling with winch | Stored Energy Over-tensioning cable | Stored energy release Plant interaction Personal injury Over-tensioning of cable Damage to cable Damage to equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0022 Cable Pulling Work Instruction SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Barricade off area of work - exclusion of unauthorised person Use non energy storing pull rope when winching Drum set up on level ground and barricade. Signage Guards to be in place as per manufacturers specifications Suitably qualified personnel to secure pulling equipment where required JHA & Take 5 Plant operated as per manufacturer's recommendations, Spotter in place Inspect condition of cable connection prior to use. Works are not to commence until the cable connection has been inspected by the Supervisor. Personnel to stay clear of inside bends while cable pulling. Stay on outside Communication - radio communication/hand signals, VSD Winch - CTO Follow VSD work procedure PPE- Impact rated gloves, hard hat, safety glasses Star Inspections | Major | Unlikely |  | M12 |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 AS/NZS 3000
Cable Termination | large, heavy cables with low flexibility Sharp edges Fauna present in electrical installations | musculoskeletal injury - strain cuts/lacerations Injury caused by contact with fauna | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0006 Manual Handling SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Team lifts Pre-task lift assessment Good manual handling technique, task stretching/warm up JHA, Take 5 Good housekeeping practices, removal of equipment and materials not required out of the work area prior to installing equipment No open bladed knives, use of specialist cable stripping tools Star Inspections Inspect installations for fauna before task commencement | Major | Possible |  | H14 |  | Site First Aiders Site Medic Emergency Channel 39 AS/NZS 3000
Work in RMUs
Working inside RMU footings | Awkward, restricted access / egress Fauna present in electrical installations | Musculoskeletal injury - strains, sprains Cuts/Lacerations Awkward egress In case of medical emergency | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Footings condition to be assessed as suitable prior to entry Access to RMU footing to be provided via ramp and fixed ladder Personnel in footings to wear lifting harness for retrieval in case of medical emergency Personnel rescue via inertia reel / rescue reel plus crane in vicinity to assist if needed Spotter to be present at all times personnel are working in footings Inspect installations for fauna before task commencement | Major | Unlikely |  | M12 |  | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Trapped Fauna | Injury to personnel Damage to equipment Injury to Fauna | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Condition of footings to be assessed prior to entry Report all fauna interactions to supervision Synergy environmental team to be advised if fauna discovered in distress | Major | Possible |  | H14
Working Inside RMU | Awkward, restricted access / egress | Musculoskeletal injury - strains, sprains Cuts/Lacerations Awkward egress In case of medical emergency | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | RMU internal condition to be assessed as suitable prior to enrty Access to RMU to be provided via ramp and fixed ladder Personnel in RMU to wear lifting harness for retrieval in case of medical emergency Personnel rescue via inertia reel / rescue reel plus crane in vicinity to assist if needed Spotter to be present at all times personnel are working in RMU | Major | Unlikely |  | M12 |  | WA Code of Practice Hazardous Manual Tasks
| Large, heavy cables with low flexibility Sharp edges Cramped working conditions | Musculoskeletal injury - strain cuts/lacerations | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0006 Manual Handling SCEE-BS-HS-PRO-0013 Personal Protective Equipment SCEE-BS-HS-GUI-0004 SCEE Minimum PPE Matrix SCEE-BS-HS-GUI-0005 SCEE Electrical Glove Matrix | Team lifts Pre-task lift assessment Good manual handling technique, task stretching/warm up JHA, Take 5 Good housekeeping practices, removal of equipment and materials not required out of the work area prior to installing equipment No open bladed knives, use of specialist cable stripping tools Star Inspections | Major | Possible |  | H14 |  | WA Code of Practice Hazardous Manual Tasks
Work in Substations
Substation entry | Slippery stairways | Slips/trips/falls | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Situational awareness Eyes on pathway | [5 empty] | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Low light conditions | Slips/trips/falls | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Clear glasses to be worn at all times when inside substations Situational awareness Eyes on pathway
Working in substations | Energised equipment | Personnel injury from electric shock and / or arc flash Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Correct arc rated clothing to be worn by personnel when necessary | [5 empty] | AS4836
Working with Batteries
Working with batteries | Energised Equipment | Personnel injury from electric shock and / or arc flash Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Out of service tags to be placed on the open battery breaker at the bottom of each of the five battery banks Detached connector lead to be removed from the container and secured in offices Battery bank container doors to be locked and keys secured in office lock box | Moderate | Unlikely |  | M7 |  | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 AS/NZS 3000 AS/NZS 3012 AS4836
| High fault current | Arc Flash | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Correct arc rated clothing to be worn by personnel when necessary
Installation of final battery links | High fault current | Electric Shock Battery Short Fire Equipment Damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Correct arc rated clothing to be worn by personnel when necessary
Testing and Commissioning
Handover of areas for commissioning | Unbarricaded areas leading to interactions between construction and commissioning activities | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Correct barricading - Hard cattle fencing or similar with blue/white commissioning tape attached All entry/exit points to be clearly marked as commissioning areas with area owner callup details present Site notice to advise of pending commissioning controlled area to be issued prior to handover | [5 empty] | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 AS/NZS 3000 AS/NZS 3012 AS4836
Working in commissioning areas | Unauthorised personnel in commissioning areas | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Online and face to face commissioning inductions to be completed by all personnel working in commissioning areas Authority to Work forms to be completed prior to entry to areas Area owner call up to be undertaken by non work related personnel entering area (Inspections etc)
| Non issuance of authority to work form prior to work commencing | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Authority to Work form complete with detailed scope of works to be completed by work crews prior to work commencing
| Non issuance of notice of energisation prior to work commencing | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Comprehensive Notice of Energisation to be completed prior to any components being energised
| Energised equipment in commissioning areas | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Correct arc rated clothing to be worn by personnel when necessary
Handover of commissioned areas to client |  |  | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan

## Steel Erection and Tilt Up
Register Type | Project Risk Register
Project(s) | CBESS BOP
Approved by
Task / Activity | Hazard | Risk (un-wanted event) | Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
Site Access And Traffic
Deliveries & Visitors to site | Short Term Workers and/or Visitors not familiar with site and/or emergency procedures | Personal injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan CBESS Project Short Term Worker and Visitor Procedure | Short Term Workers and/or visitors to be managed by Responsible Person or Escort Visitors to sign in on arrival to site | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Construction Vehicle Site Access / Vehicle movements to and from site | Vehicle and/or personnel collision | Personal injury Property damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Traffic Management Plan to be made available Correct signage to be displayed JHA/Take 5 | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
General Construction Activities
Penetrations and Wall Openings | Penetration covers not adequate to take loads imposed | Personal injury Damage to construction Vehicle damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Penetrations over 150mm in diameter to have mesh cast in and covered in accordance with Industry Practice Column, beam penetrations in formwork to be covered and secured with F81 mesh or handrails Large mechanical penetrations to have temp handrail fitted, completed with mesh and kickboards Lift openings to be fully meshed, until such times as lockable lift gates are fitted | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Person(s), materials falling | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Penetrations over 150mm in diameter to have mesh cast in and covered in accordance with Industry Practice Column, beam penetrations in formwork to be covered and secured with F81 mesh or handrails Large mechanical penetrations to have temp handrail fitted, completed with mesh and kickboards Lift openings to be fully meshed, until such times as lockable lift gates are fitted | Catastrophic | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Falls
| Wall openings not covered | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Penetrations over 150mm in diameter to have mesh cast in and covered in accordance with Industry Practice | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Struck by falling objects | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Penetrations over 150mm in diameter to have mesh cast in and covered in accordance with Industry Practice Column, beam penetrations in formwork to be covered and secured with F81 mesh or handrails Large mechanical penetrations to have temp handrail fitted, completed with mesh and kickboards Lift openings to be fully meshed, until such times as lockable lift gates are fitted | Catastrophic | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Partitions, Doors ,Baffles and Ceilings | Exposure to dust | Personal injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | PPE to be worn at all times. P2 masks to be worn when exposed to dust. Debris to be regularly cleared from work area and dust control measures to be put in place. | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Breakage of glass | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | PPE to be worn at all times, Clear Glass to be marked with tape. | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Roofing/Working At Heights | Adverse Weather Falls from height | Personal injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | No working on roof when raining or icy conditions Hydration breaks/adequate sun protection in hot sunny conditions If there is moisture on roof, risk assessment must be conducted prior to working on roof. | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Falls
Scaffolding Activities
Erection, dismantling and Altering | Scaffold collapse Fauna present in scaffold tubes and joints | Personal injury Equipment damage |  | Drilled in anchors, whether expanding or chemical types that are subject to tensile loads shall only be used where it is not practicable to secure or tie the scaffold in any other way. An assessment of the material to which the drilled-in anchors are supplied shall confirm their suitability for the application. Scaffold tubes and joints to be inspected for fauna before use All platforms shall be capable of supporting their design loads. Platforms to be closely decked such that a gap between individual decking components in a bay is not greater than 10mm. Steel fixing wire shall not be used to secure planks. Where materials are stored on a working platform, a clear and unobstructed access of not less than 450mm shall be maintained. The minimum unobstructed access of any working bay shall not be less than 450mm, regardless of the shape. Edge protection shall be provided at the open ends and sides of all platforms, landings and along temporary stairways from which a person or object could fall a distance exceeding 2m. Guard rails shall be set at a height of not less than 900mm above the platform and no greater than 100mm outside the edge of the platform Toe boards shall not extend less than 150mm above the working platform surface. Edge protection shall be comprised of one of the following; Guard rails, mid rails and toe boards / Guard rail panels / Guard rail and in fill panels The clear width of an access platform shall not be less than; 450mm for persons and hand tools only. 675mm for persons and materials 900mm for emergency access. Safe Work method statements for trades utilising the scaffold to access their activity are to nominate that no scaffold is to be altered or erected unless by it is completed by a certified scaffolder with applicable training for the task and with permission given from HALLSTON Management Regular inspections to be completed by HALLSTON foreman and Site OHSE Consultative process Access openings and stairways shall be free of sharp edges and points that could cause injury Incomplete scaffolds are to display appropriate signage and have measures erected or in place that will stop unauthorised use. Scaffold and handrails not to be removed without approval Handrails, midrails, kickboards to be in place Ladders to be inspected regularly for defects and clearly labelled for industrial use HaAll scaffolds where item and/or object can fall 4m or more to be erected by licensed scaffolders. Scaffold to be installed as per reviewed drawings and modified and maintained in a safe manner Scaffold to be adequately tied or racked as per engineers design Scaffold to be set on firm footing and protected from plant movements. Regular inspections and sign off required Incomplete scaffolds are to display appropriate signage Loading bays to be signposted with the engineered Safe Working Loads and is not to be exceeded. | Catastrophic | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Scaffold Usage | Use of incomplete / inadequate scaffold | Personal injury Equipment damage |  | Scaffolds erected in accordance with Australian Standard requirements. Use Scaffolding Checklist (WHS 038) A Design Plan shall be provided on the scaffolding system/equipment where required by legislation. The plan shall include; - basis of design - foundations (including ground conditions) - the weight bearing capacity of the surface where the scaffold is to be erected. - size and weight of the scaffold (for example, dead, live and environmental loads) - supporting structure - access and egress - tying and anchors (that is, where anchors will be placed on the supporting structure; and types of anchors to be used) - bracing - type of scaffold - edge protection. Handover certificate to be issued by scaffolding contractor prior to scaffold being used, after each 30 day inspection or when scaffold is altered. Scaffold is to be categorised by the scaffolder; Light, Medium or Heavy Duty All scaffolds where item and/or object can fall 4m or more to be erected by licensed scaffolders. Scaffold to be installed as per reviewed drawings and modified and maintained in a safe manner The location and tie systems shall not obstruct clear access along the full length of any working platform or access way. | Catastrophic | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Structural Steel Works
Structural Steel Erection | Unstable base for crane causing crane to tip whilst erecting steel Structural collapse after erection | Personal injury Equipment damage |  | Location of Crane outriggers satisfies the sub base strength on suspended slab or made up ground (geo tech or engineers reports) Prior confirmation that there will be no services located under the outriggers. Safe methods of installation to prevent falls are to be established. Including the use of mobile cranes, scissor lifts, boom lifts Area below to be barricaded off & warning signage displayed where required Ticketed Riggers to erect and install Approved lifting methods using chains and slings to be in place. Chains and slings to be tested, inspected and in date prior to use Engineer sign off for all structural elements | Catastrophic | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Manual Handling
Manual Movement of Materials and Equipment | Repetetive strain injuries Muscle strain/strain Sharp edges on materials | Personal injury |  | Safe Work Procedures to be drafted as part of the subcontractor’s Safe Operating Procedures/SWMS Where possible, mechanical methods of lifting should be implemented. Where this is not possible, team lifting is to be utilised Personnel undertaking manual tasks to be inducted into safe working procedures Correct PPE for task | Moderate | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Plant, Equipment and Tool Usage
Usage of Hoist | Use of incomplete or inadequate hoist | Personal injury Equipment damage |  | Hoist to be erected in accordance with Australian Standard requirements Documented information, written in plain English shall be provided on the hoist equipment. The documentation shall include; Supplier and the means of product identification A list of all components with descriptions from which each can be identified Instructions for erection, dismantling, use, transportation and storage Guidance for servicing and inspection of the equipment and the rejection of damaged components Nominal weight in kilograms Details giving sufficient information to determine; duty loadings, max heights, max location of ties, Handover certificate to be issued by company installing hoist contractor prior to hoist being used, Daily pre-inspection to be carried out by competent person; Periodic inspections in accordance with manufacturers/suppliers specifications; SWL to be clearly displayed; All hoists erected, altered and/or dismantled by licensed riggers; Hoist to be installed as per reviewed drawings and modified and maintained in a safe manner The location and tie systems shall be in accordance with the engineer’s requirements; Hoist enclosure to be installed in accordance with Australian Standards AS 2550.7 & AS 1418; Steel fixing wire shall not be used to secure the enclosure; Drilled in anchors/ties, whether expanding or chemical types, which are subject to tensile loads, shall only be used where it is not practicable to secure or tie the hoist in any other way and the engineer has specified there use. An assessment of the material to which the drilled-in anchors are supplied shall confirm their suitability for the application. Regular visual inspections to be completed by Site Foreman and Site OHSE Consultative process; Incomplete hoists are to display appropriate signage and have measures erected or in place that will stop unauthorised use | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Untrained/unqualified personnel operating hoist | Personal injury Equipment damage |  | Hoist to be operated by competent person or trainee under direct supervision of a competent person; Hoist to have daily pre-use inspection completed by a competent person with details recorded in log book; Hoist operator to continually lookout for obstructions and notify supervisor of any foreseeable problems; Operator to review swms and amend as required prior to signing; Operator to secure hoist to prevent unauthorised use; | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Loading Platforms | Personnel falling whilst installing, relocating, and/or removing loading platforms | Personal injury |  | SWMS to be provided for the installation, relocation and/or removal of Loading Platforms; Loading Platforms to be installed by qualified rigger/scaffolders’ Edge protection to be removed from area where loading platform is to be installed only; Edge protection to be re-installed after loading platform is relocated and/or removed; Fall restraint equipment to be worn where edge protection is not provided; Appropriate size crane to be used; No materials, equipment and/or personnel to be on the platform whilst platform is being moved; Area below installation, relocation and/or removal to be barricaded off if there is a risk of any materials /debris falling; Regular inspections to be carried out to ensure loading platforms are secure | Catastrophic | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Falls
| Incorrect usage of loading platform | Personal injury Equipment damage |  | Gates to remain closed and secure when loading platform not in use; Gates to be closed once load has been landed or removed. Only Only designated personnel to open/close gates; SWL to be clearly displayed and not exceeded | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Explosive Power Tools | Unauthorised use | Personal injury Equipment damage |  | Only trained and competent persons to use EPT | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| EPT not maintained in accordance with manufactureres instructions | Personal injury Equipment damage |  | EPT to be maintained in accordance with Australian Standards and manufacturers requirements Do not point at other persons Only trained and competent persons to use EPT EPT to be loaded immediately prior to use only | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Electrical Works
Working Near Powerlines | Over head powerlines in vicinity | Personal injury Equipment damage |  | Signpost “Overhead Powerlines” at site entrance | Moderate | Rare |  | Rare |  | Site First Aiders Site Medic Emergency Channel 39
| Working with electrical equipment | Personal injury Equipment damage |  | Working on or near live power is not permitted, unless process is signed off by HALLSTON Construction Manager in accordance with electrical requirements applicable to the Local Statutory Authority All temporary distribution boards to be tested by a qualified electrician upon installation and periodically tested as required by local legislation. Refer local Legislation & applicable Codes Live power supply to main switchboards not covered by earth leakage protection should be adequately protected and signed Works undertaken after permanent power supply has been installed and ELCB does not exist will require persons to use portable earth leakage devices Lock Out Tag Out procedure to be developed along with register. Temporary electrical carried out in accordance with AS/NZS 3000 & AS3012 and local legislative requirements Permanent electrical to be carried out in accordance with AS/NZS 3000 Switchboards to be fitted with Class 2RCDs Extension leads to be elevated on insulated hooks or stands All electrical equipment to be inspected tested and tagged prior to use in accordance local requirements by a qualified person. i.e. Regulations and/or codes of practice. Tagging Register to be updated monthly. | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Working At Heights
| Fall from height | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan WHS-SWP-004 Working at Heights; SYN-PRC-HAS-0010 Safe Work at Height Procedure | Safe Work Method Statement required for works where a person can fall. Fall restraint or fall arrest to be used 2m exclusion zone from edge Static lines and harness with lanyards to be used where necessary Fall restraint/arrest equipment i.e. safety harnesses are only to be used as a last resort and only then after consultation with HALLSTON Site Management, except where it is a legislative requirement i.e. Boom Lift Emergency procedure developed with the SWMS. Workers are not to work alone Perimeter of building to be protected using scaffolding, fencing, or screens Handrails to be installed ASAP after concrete floor slab has been poured, prior to stripping formwork where possible but prior to the raising of the perimeter screens Penetrations over 150mm in diameter to have mesh cast in and covered in accordance with Industry Practice Column, beam penetrations in formwork to be covered and secured with F81 mesh or handrails Large mechanical penetrations to have temp handrail fitted, completed with mesh and kickboards Edge Protection installed to be in accordance with AS 1576. Work zones to be barricade/bunted off to highlight exclusion zones for workers below and moving plant | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Falls
| Lack of training for personnel in the use of fall restraint/arrest equipment | Personal injury Equipment damage |  | Workers to have current W@H qualification W@H permit to be utilised | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Falls
| Lack of edge protection Penetrations not covered Wall openings not covered | Personal injury Equipment damage |  | Edge Protection installed to be in accordance with AS 1576. Safe Work Method Statement required for works where a person can fall Penetrations over 150mm in diameter to have mesh cast in and covered in accordance with Industry Practice Column, beam penetrations in formwork to be covered and secured with F81 mesh or handrails Large mechanical penetrations to have temp handrail fitted, completed with mesh and kickboards Safe Work Method Statement required for works where a person can fall Perimeter of building to be protected using scaffolding, fencing, or screens | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Falls
Tilt panel Construction
| Incorrect design of panel | Personal injury Equipment damage |  | The design for pre-cast or tilt up panels must be verified for compliance with AS 3850 by a qualified Engineer. Drawings for the erection of the panels must include details on how the panels are to be placed and secured into position. Information to be shown on these drawings includes: • Date and issue number of the drawing. • Project location. • Position of brace connection points on the panel and the ground. • Brace specifications and/or required capacities. • Leveling pad details. • Relative locations of panels. • Details for brace footings including dimensions, location, anchor type, and concrete strength at time of erection. • Details on knee and lateral bracing (if applicable) Tilt-Up and Pre-cast COP | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Site planning hazards Poor work area | Personal injury Equipment damage |  | Project team and relevant subcontractor must discuss and agree on, but not limited to: • The location of casting beds (tilt up panels) relative to the erection location for the panels. • The travel paths for concrete trucks (tilt up panels), semi-trailers (pre-cast panels), mobile cranes (erection), EWP’s (bracing inserts, grouting, etc.). • The required ground / engineered surface conditions for the placement of panels. • The location of any services (above or below ground) which may impact or be impacted by the activity. • Any other requirements related to the work activity or required risk controls. Supervisor to have completed Tilt-Up panel Supervisor training TILT UP CONSTRUCTION FOR SUPERVISORS Course Code ATM011A Workers to have Tilt-Up panel training CPCCCM1016A Identify requirements for Identify requirements for safe tilt-up work 51203 Course to Contribute to Safe Tilt-up Construction; 51629 Course in Contribute to Safe Tilt-Up Construction; CPCCCM1007A Carry out tilt-up work safely; or CPCCCM2011A Carry out tilt up work safely Site inspection to be carried out for panel erection works by contractor and site manager prior to works starting. Laydown plan developed and any hazards removed. | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Regulator not notified | Damage to reputation |  | At least 10 days prior to the casting of any panels, WorkSafe WA must be notified in writing of the event. A copy of the WorkSafe WA approval must be supplied to the contractor. The approved form must be held on site for the duration of the panel manufacturing period. | Major | Rare |  | Rare |  | Site First Aiders Site Medic Emergency Channel 39
| Traffic movement causing harm or damage during casting, erection and bracing | Personal injury Equipment damage |  | TMP to be developed and site notice s issued at pre-start Casting An exclusion zone - relative to work area around casting beds must be implemented.This provides room for the delivery and placement of reo and concrete, including curing requirements. Erection An exclusion zone equal to at least 1.3 times the height of the panel to be implemented around all sides of the panels. Where panels are erected on suspended surfaces, exclusion zones must be relative to the height of the panel Site notice to be issued Bracing After erection of panels and installation of bracing, an implemented on the braced side of the panels. The zone must be of sufficient size to prevent contact with operating Plant. Where practicable, consideration must be given to implementing an exclusion zone on the non-braced side of panels, to mitigate contact of Plant with the structure | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Plant in the Workplace
| Damage injury from rotation of panels during placement | Personal injury Equipment damage |  | Ticketed Riggers to erect and install Barricading and warning signage to be in place The distance from the auxiliary winch rope lifting point to the end of the panel is not to exceed 1/4 of the panel length. The included angle between the main hoist rope and auxiliary hoist rope is not to exceed 45 degrees. Panels to be rotated so that the panel is suspended in its rotated position by the main winch (if one Crane used), or the larger capacity Crane (if two Cranes are used). Panel to be adequately reinforced to withstand the lifting stresses. If the conditions above cannot be complied with an Engineer must verify the minimum required capacity of the hoist ropes | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Working at heights | Personal injury Equipment damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan WHS-SWP-004 Working at Heights; SYN-PRC-HAS-0010 Safe Work at Height Procedure | The type of fall from height protection or falling objects protection to be implemented during the work activity will be determined by assessing the risk of the work activity to be completed. Work activity at height is managed using any or all of, but not limited to: Installation of proprietary edge protection and / or scaffolding. Where required, wrapping edge protection with shade cloth to prevent objects from falling through handrails, etc. Use of Elevated Working Platforms (EWP) – e.g. Boom or Scissor Lifts. Use of Personnel Protective Equipment (PPE) – e.g. harnesses, static lines. Ensuring that working surfaces are slip free. Ensuring that access / egress locations are suited to the work activity and are free of obstructions. Ensuring protection / covering of surface penetrations / holes | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
| Lifting and installing panels | Personal injury Equipment damage |  | Panels should be suspended with their face as near to vertical as practicable. Braces, whenever possible should be attached to the concrete panel prior to lifting. The bottom edges of panels should be horizontal. Lifting clutch release lines to be fitted so that the clutches can be disengaged without the need for workers to climb on top of the panel. Dowel pins to be fitted into the bottom edge of the panels or into the footings prior to lowering. Crane supports are to be maintained until all braces have been installed and effectively secured to the panel and footings. | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39
Painting On Site
| Contact with hazardous materials Release of hazardous materials | Occupational asthma, skin sensitisation, respiratory disease, cancer Environmental impact from spilt chemicals | BIS-SWMS-019 – Painting on site | Adequate ventilation and other necessary safety precautions should be provided when using solvent based products, particularly in enclosed spaces Wear safety goggles to protect eyes from splashing and overspray Check SDS for respirator requirements, such as half face with organic cartridge: Latex paint: No respiratory equipment if well ventilated, long pants/ sleeves or coveralls Oil based: Air purifying half face mask with organic vapour cartridge, safety glasses, coveralls (Tyvek) Isocyantate-containing: Supplied air, hooded Tyvek suit Ensure spraying is not done upward, as this directs spray into breathing zone and face Mix minimum quantity of paint necessary Ensure flammable liquid containers are grounded during pouring Ensure chemical impervious gumboots and protective clothing is worn Ensure ground around work area is covered before using paint Ensure waste paint and containers are disposed of correctly Ensure spill kits are available to the work area, and workers are trained in their use | Major | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Hazardous Chemicals in the Workplace WA Dangerous Goods Safety (General) Regulations 2007 WA Dangerous Goods Safety Act 2004
| Fluid under pressure | Personal injury Environmental impact | BIS-SWMS-019 – Painting on site | Spray gun hoses are routed as straight as possible to avoid kinking Any water condensation is drained from the compressed air system Satisfactory pressure for the operation of the spray gun Spray gun is held perpendicular to the surface area being sprayed at all times, with the air line held back away from the item Work arranged to minimise exposure. Be aware of wind direction, avoid spraying into wind (rotate work – not operator) Ensure system is set to reccomended operating pressure to avoid excessive overspray Staggered work positions to avoid overspray of the operators Spray gun pointed only at the work – never at yourself or another person Spraying is not done in upward direction, as the directs spray into breathing zone and face Dispose of waste paint and containers appropriately Ensure spill kits are available to the work area, and workers are trained in their use | Severe | Unlikely |  | Unlikely |  | Site First Aiders Site Medic Emergency Channel 39

## Transformer Skating
Register Type | Project Risk Register
Project(s) | CBESS BOP
Approved by
Task / Activity | Hazard | Risk (un-wanted event) | Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
Mobilising to and around Site
Site Access-Entering The Site, Moving Within The Site, Moving To And From Work Area. | Contact with vehicles Contact with plant /equipment Contact with personnel | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0022 Journey Management Procedure | All delivery drivers to complete the appropriate inductions prior to arriving at site. Semi trailers are to be piloted by staff into position. Work area to be isolated and barricaded to prevent unauthorised access. Spotter to be onsite to redirect traffic where necessary. Constant radio communication to be maintained with the driver. Driver to remain clear of all structures and persons. Follow SYNERGY/ SCEE's TMP on site | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Trucks Entering Site | Traffic hazard Contact with Vehicles | Road Blockage or Damage to trailer and or equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0022 Journey Management Procedure | Trucks to follow Main road permit and approved route details Trucks to enter under guidance of staff and in accordance with the delivery plan. Supervisor to monitor traffic movements. Ensure trucks reverse beacons and warning sound is working and maintained. Follow SYNERGY/ SCEE's TMP on site | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
Truck Movement and Parking on Site
| Traffic hazard Interaction with personnel | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Trucks to enter under guidance of staff and in accordance with the delivery plan. Supervisor to monitor traffic movements. Follow SYNERGY/ SCEE's TMP on site | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Ground conditions | Damage to trailer Damage to equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan 201074-SE-PRO-001 Barricading Signage and Exclusive Control | Ground conditions to be inspected to ensure suitability for trailer offload and task commencement Task area to be suitably barricaded and appropriate signage displayed | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Transformer Skating
Project Documentation and Overview | Lack of information and/or Instruction JHA not completed | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Ensure JHA’ and/or SWMS s are completed, reviewed and signed off prior to conducting works. Ensure all team members read and understand the JHA and Procedures for the task. Attend SCEE's pre-start meeting daily. Pre-start meeting starts at 06:30 am | Moderate | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
| Weather Events - Working in direct sunlight | Heat stress and dehydration | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Use Suncreen / Sunhat if needed Ensure adequate water supply Monitor for heat related illness Hydration tests as required | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
Set Up Crane/ Jack And Skate gears | Manual handling Injuries Repetitive strain Injuries Muscular injury due to repetitive work | Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0026 Crane Activity SCEE-BS-HS-SWM-0019 General Mobile Crane Work SYN-PRC-HSA-Synergy Lifting Operations Procedure | Warm ups excercised before work commencement Always use correct manual handling techniques when lifting. Use of mechanical lifting devices and trolleys where possible. Stability of load to be check prior to unloading / removing of tie down straps, to ensure load has not shifted during transportation to site Delivery driver to remove tie down straps. | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39 WA Code of Practice Hazardous Manual Tasks WA Code of Practice Managing Risk of Plant in the Workplace
| Faulty Hiab Faulty Rigging Equipment | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0026 Crane Activity SCEE-BS-HS-SWM-0019 General Mobile Crane Work SYN-PRC-HSA-Synergy Lifting Operations Procedure | Pre-start to be completed on Franna/cranes, all faults to be reported All lifting gear is to be inspected for damage or faults and correctly tagged. Any lfting gear found to be damaged or faulty to be tagged out of service and reported Load to be inspect prior to lift to ensure there are no sharp edges to damage or shear soft slings. Packing to be used to protect soft slings from sharp edges. Maintain Safe working load at all times. | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Hydrocarbon release to environment | Hydrocarbon spill from oil transfer or mobile plant entering environment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0021 Hazardous Materials Handling and Storage | Spill kit, on plant where practicable; Regular maintenance of plant Plant premobilisation check prior to use on site Plant risk assessment Daily prestart check of plant Should a hydraulic leak develop, stop using the plant as soon as safe to do so and remove from service Use of absorbent pads/sausages if required Ensure personnel are trained in the use and disposal of spill kits and contaminated materials | Moderate | Unlikely |  | Low |  | Notification of event to Synergy Enviromnental Representative as soon as possible Site Security Site Medic Emergency Channel 39
Assembly Of Transformer
| Equipment not connected correctly causing load to drop from height Inappropriate set up Failure of Equipment | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0026 Crane Activity SCEE-BS-HS-SWM-0019 General Mobile Crane Work SYN-PRC-HSA-Synergy Lifting Operations Procedure | Equipment must be set up by appropriately experienced and competent persons. Beams to be packed where necessary All equipment is to be inspected prior to use and after use. Damaged equipment is to be removed immediately and tagged out of service All equipment to be rated to load capacities as indicated by engineers instructions. Use berk bars to line up beams parallel with Transformer. Connect beams together as per manufactures guidelines. Perform visual inspection of equipment prior to lift. Damaged equipment is to be removed immediately and tagged out of service Site supervisor to check setup prior to lift. Check for line of fire hazards | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Crush injury / line of fire | Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Clear communication to be maintained All non-essential personnel to be removed from work area. Raise/lower all pods at the same rate and maintain constant visual watch. Place stands under Transformer once raised. Trailer to be locked out to ensure there is no movement during unload of transformer | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Hydraulic hose failure | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Check hoses for leaks prior to use. Ensure all connections are secure and hoses are attached to respective jacks. Spotters to observe movements to ensure all secure. Ensure the spill kit is available, accessible, and its contents are checked. Ensure personnel are trained in the use and disposal of spill kits and contaminated materials. All equipment is to be rated to load capacities as indicated by engineers instructions. Only essential staff to be present in work area. | Moderate | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Working on top of transformer
| Falls From Height | Personal Injury | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0017 Working at Height (High Risk) Procedure | Use of platform ladders with back bar Fall prevention harness and lanyard to be worn where applicable All non platform ladders to be securely tied to structure and fall prevention equipment utilised when in use | Catastrophic | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39 WA Code of Practice Managing Risk of Falls
Setup Vacuum Plant, Oil Treatment Plant And Generator
| Faulty Electrical equipment Incorrect connection of electrical equipment Electric Shock | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | All electrical equipment to be tested prior to energisation All portable equipment to be tested and tagged quarterly All electrical equipment to be Australian or IEC certified All isolation and energisation procedures to be followed Ensure all connections from generator are done by a licensed Electrician | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Running Of Plant For Vacuum Fill.
| Oil Spillage | Contractual or legislative damage Damage to plant or equipment Injury to personnel Environmental impact | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0021 Hazardous Materials Handling and Storage | Minimise trip hazards where possible Ensure spill kit is available, accessible, and its contents are checked. Ensure personnel are trained in the use and disposal of spill kits and contaminated materials. IBC's to be lifted only with appropriate lifting device and stored inside the bund where possible Appropriate PPE to be used by all personnel, including Nitrile gloves to avoid oil contact Visual inspection of hoses to be done prior to use While oil circulation and filling is in process constant monitoring required No entry into area without approval while filling in process Exclusive control barricading and appropriate signage to be set up around area SDS to be available | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
| Oil splash | Injury to personnel Environmental damage | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0021 Hazardous Materials Handling and Storage | Ensure all workers for the task are wearing appropriate PPE, including Nitrile Gloves to avoid contact with skin Spill kits as necessary | Minor | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Impacts from plant | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Ensure Site Emergency procedures are followed Fire Extinguishers available in case of fire Ear protection to be used as required | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Stop Plant And Disconnect Generator
| Electric Shock | Electric Shock To Personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Switch off generator, ensure all disconnects from generator are done by a licensed Electrician | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Touch Up Painting
| Paint Splashed in Face Paint spill to ground | Eye Injury Environmental impact from chemical spill | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-WIN-0021 Hazardous Materials Handling and Storage | Ensure correct PPE is worn during painting operations Ensure any spills are cleaned up promptly, follow CCC procedure SDS to be available All contaminated waste to be disposed of correctly | Moderate | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Demobilisation from site
| Personnel exposed to plant/vehicle movements | Blocked access Personnel in area Other vehicles | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Work Group to guide equipment off site Spotter to be onsite to redirect traffic where necessary. | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39

## Install Roof Sheeting
Register Type | Project Risk Register
Project(s) | CBESS BOP
Approved by
Task / Activity | Hazard | Risk (un-wanted event) | Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
Install Edge Protection, Safety Mesh, insulation and roof cladding
| Fall from height | Injury to person | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Working at Heights Training and competency assessment of all workers exposed to falls from height. (WP-VOC & WAH training) All work at Height control measures are to maximise the use of fall restraint. Fall Restraint / Arrest Systems to be utilised at all times where the potential to fall from height exists. These situations will be identified by supervision during pre-task methodologies and risk assessments. Edge protection around roof, i.e. RHS Railing erected full perimeter. AS 1657:1992 and fall restraint harness with a web loop or static line (dependent upon accessibility). Anchored safety harness to be worn at all times in EWP's. If area is restricted, slow speeds to be adhered to, checking clearances prior to movement, trained and assessed spotter to be used in these areas. SCEE WAH Permit shall be utilisied. All WAH equipment shall be inspected and tagged as per quarter. Fall restraint preferred method of hook up Rescue Plan in place specific and detailed to include when in Suspension and when Stranded at height. Personnel to remain in 100% hook up until they are within the roofs edge protection | Moderate | Unlikely |  | Mod 9 | Accept | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022 WA Code of Practice Managing Risk of Falls
| Falling Objects | Injury to person | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Exposed edges or penetrations to be protected. Small tools to be restrained at height using tool lanyards and small materials in buckets. Area below EWP and roof installation shall be barricaded off to prevent access. Complaince to SCEE's SEE (Secure/Encapsulate and Exclude requirments) Consider deflection of dropped objects when setting up drop zones. Work crew to have to monitor wind speeds during the shift. | Moderate | Unlikely |  | Mod 9 | Accept
| Poor Access/Egress | Injury to Person | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Access to roof shall be via EWP. Employees shall exit EWP basket on full meshed roof. 100% hook up shall be maintained when operating EWP, with spotters in place. Approved SWMS/Methodology shall be in place before works commence. SCEE WAH permit & rescue plan in place HRWL-WP, VOC & WAH Training | Moderate | Unlikely |  | Mod 9 | Accept
Cutting and Installation of Roof Cladding
| Incorrect Manual handling | Injury to person | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Use of mechanical lifting equipment to eliminate manual handling where possible. Training of personnel on correct manual handling techniques. (SCEE manual handing training) Team lifts as required. Crane to be utilized for lifting structural and roof covering materials. All materials to be secured to prevent them from being wind-blown. Installed Roofing sheets to fully secured prior to the work team leaving the job site to prevent them being blown off the roof. (Screwed Off) | Moderate | Rare |  | Low 5 | Accept | WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
| Incorrect selection and use of equipment | Injury to person/ hand injuries | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Check equipment before and after use. Correct insulation with hand tools used for electrical works. Current test and tag (electrical equipment). Testing of RCD's everyday prior to usage. Competent operators. Correct PPE and clothing to be worn. Deadman switches. Tag out protocol. Lift indicators installed on cranes. | Moderate | Rare |  | Low 5 | Accept
| Loss of control of loads, including loose / falling loads | Injury to person | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Loads to be checked once weight is taken. VOC process for riggers. 16mm Tag lines to be used to control loads at all times. Lifts are to be planned prior to hoisting and a clear understanding between the Rigger / Dogman and Crane Driver maintained at all times. Use nominate lifting points. No lifting over personnel, plant or vehicles. No one to get underneath a suspended load. Steel loads to be double wrapped. Refer to Method Statement for task. | Moderate | Unlikely |  | Mod 9 | Accept

## Gantry Works in Switchyard
Register Type | Project Risk Register
Project(s) | CBESS BOP
Approved by
Task / Activity | Hazard | Risk (un-wanted event) | Systems Policy, Plans & Procedures | Controls | Consequence | Likelihood | Calc. | Residual Risk / Impact | Accept or Reject | Recommended Additional Controls | By Whom Person to Action | Target Date | Zone / Area Of Special Interest
Bucket Lift Truck Compliance
Non compliant vehicle | Missing vehicle prestart checks Missing EWP inspections | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan AS 1418 | Ensure correct certification to relevant parts of AS1418 Vehicle certified by competent person Ensure vehicle prestart completed before use Ensure EWP has inspection completed before usse | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
Mobilising Bucket Lift Truck to Site
Site Access-Entering The Site, Moving Within The Site, | Contact with vehicles Contact with plant /equipment Contact with personnel | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Appropriate inductions to be completed prior to arriving at site. Operator to hold correct tickets for vehicle. Work area to be isolated and barricaded to prevent unauthorised access. Spotter to be onsite to redirect traffic where necessary. Constant radio communication to be maintained with the operator. Operator to remain clear of all structures and persons. | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39 WA Work Health and Safety Act 2020 WA Work Health and Safety (General) Regulations 2022
Bucket Lift Truck Operation
Moving bucket lift truck to task area | Incorrect operation of vehicle | Injury to personnel Damage to equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Qualified, trained and experienced operator. Operator to read, understand and sign on to task JHA | Moderate | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
| Inadequate ground conditions | Vehicle instability when moving Injury to personnel Damage to equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Ground to be inspected by qualified personnel before task commencement | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
Bucket lift truck set up at task area | Inadequate ground conditions Incorrect setup of truck | Vehicle unstable during usage Vehicle tip over during EWP use Muscle strains during set up Damage to equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Machine set up by qualified personnel Use of mechanical lifting devices and trolleys where possible Risk assessment must be undertaken covering all operating processes and environments associated with this item of plant. | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39 WA Code of Practice Hazardous Manual Tasks WA Code of Practice Managing Risk of Plant in the Workplace
Elevated Work Platform Operation
Performing works on Switchyard gantries | Falls from Height | Injury to personnel Damage to Equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan SCEE-BS-HS-PRO-0017 Working at Height (High Risk) Procedure | Working at Heights Training and competency assessment of all workers exposed to falls from height. (WP-VOC & WAH training) All work at Height control measures are to maximise the use of fall restraint. Fall Restraint / Arrest Systems to be utilised at all times where the potential to fall from height exists. These situations will be identified by supervision during pre-task methodologies and risk assessments. Edge protection around roof, i.e. RHS Railing erected full perimeter. AS 1657:1992 and fall restraint harness with a web loop or static line (dependent upon accessibility). Anchored safety harness to be worn at all times in EWP's. If area is restricted, slow speeds to be adhered to, checking clearances prior to movement, trained and assessed spotter to be used in these areas. SCEE WAH Permit shall be utilisied. All WAH equipment shall be inspected and tagged as per quarter. Fall restraint preferred method of hook up Rescue Plan in place specific and detailed to include when in Suspension and when Stranded at height. Personnel to remain in 100% hook up at all times while in bucket | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Untrained EWP operator | EWP collision with Gantry Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Trained, competent EWP operator | Major | Almost Certain |  | Low |  | Site Security Site Medic Emergency Channel 39
| Dropped tooling | Injury to personnel Damage to Equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Tool lanyards to be used on all tooling utilised at heights | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Restricted Access | Injury to personnel Damage to Equipment | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Competent EWP operators Spotters to be utilised at all times EWP is operating Clear communication between spotters and EWP operators | Major | Likely |  | Low |  | Site Security Site Medic Emergency Channel 39
| Inclement Weather | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | BOM to be consulted prior to task commencement Lightning protocols to be followed in the event of a storm | Moderate | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Task Completion
Bucket Lift Truck demobilisation | Truck demobilised by untrained personnel | Damage to plant or equipment Injury to personnel | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Machine demobilised by qualified personnel Use of mechanical lifting devices where required. | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39
Demobilisation from site
Leaving task area and site | Personnel exposed to plant/vehicle movements | Blocked access Personnel in area Other vehicles | 201074-SE-PLN-001 Collie Battery Energy Storage Project Health, Safety and Environment Plan | Work Group to guide equipment off site Spotter to be onsite to redirect traffic where necessary. | Major | Possible |  | Low |  | Site Security Site Medic Emergency Channel 39

## Matrix
CONSEQUENCE
LIKELIHOOD | Minor | Moderate | Major | Severe | Catastrophic
Almost Certain | Medium 6 | Medium 10 | High 16 | Critical 21 | Critical 25
Likely | Low 4 | Medium 9 | High 15 | Critical 20 | Critical 24
Possible | Low 3 | Medium 8 | High 14 | High 18 | Critical 23
Unlikely | Low 2 | Medium 7 | Medium 12 | High 17 | Critical 22
Rare | Low 1 | Low 5 | Medium 11 | Medium 13 | High 19